## Design Specifications
Design Consumption | 600 | L/Day |  |  | 75.38%
Subsystem | Component | Input
Rainwater Collection | Roof Catchment |  | None
Half Roof
|  | y | Whole Roof
| Additional Catchment | y | y/n
|  | 20 | Area (m^2)
Location
|  | 5 | x (m)
|  | 10 | y (m)
| Collection Tank | 10000 | L
Storage | Storage tank volume | 27 | m^3
| Tank Location | 5 | x (m) | Height(x,y)
|  | 25 | y (m) | 10
| Storage tank tower | n | y/n | ADDS TO HEIGHT AND COST
h (m)
Pump | Pump | y | Pump A
Pump B
Pump C
None
Filtration | Filter Location |  | Pump Line
|  | y | Demand Line
| Filtration Components | y | 1um
5um
|  | y | 200um
Disinfection | UV | y | 36W
50W
| Chemical | y | Chlorine
Ozone
Power System | Power Strategy |  | Solar
|  | y | Diesel Generator
| Number of Batteries | 2 | #
Solar Power System | Model |  | HES-260
SW-80
HES-305P
| Quantity of Panels |  | #
| Inverter |  | 2.8kW DC-AC Inverter
Diesel Generator | Diesel Generator | y | 4000W 2 cyl. Diesel

## Satisfaction Values
Attribute | Value | Units | Satisfaction | Weight | Min.Val | Max Val | Cost (5 years) |  | Maintenance calculations | # of maintance / 5 years | # of maintance / year | Overall Maintenence | Overall Reliability (2014) |  | Overall Reliability (2015) |  | Average reliability
Consumption | 600 | L/day | 100% | 20% | 135 | 600 | Catchment (area, 2 tanks, tower) | 12775 | Pump (always 0) | 1 | 0.2 |  |  | 0 |  | 0 | 0
Relative Cost | 45.1% | % relative to shipping water | 90.36% | 25% | 25% | 125% | Filters | 6975 | Filters | 108 | 21.6
Health and environmental risk exposure | 47.9276 | N/A | 30.05% | 10% | 0 | 35 | Disinfection | 3100 | Disinfection | 120 | 24
Power system greenhouse gas emissions | 66.23% | % relative to shipping water | 37.89% | 10% | 20% | 100% | Pumps | 1160 | Total | 227 | 45.4
Maintenance occurences | 45.4 | #/year | 48.95% | 10% | 15 | 75 | Power | 6972.4198
On demand flow rate | 29.8066 | L/min | 84.26% | 10% | 15 | 35 | Cost For Days System Does Not Supply | 3187.5
Reliability | 322.5 | days/year | 84.5% | 15% | 200 | 365 | Total | 34169.9198
TOTAL |  |  |  | 75.38% |  |  | Shipinng water for 5 yrs | 80000

## Catchment Area
Parameters | Value | Units
Catchment_roof | 100 | m^2 |  |  |  |  | Storage Tank |  | Cost |  | Total water collected (for pumps)
Catchment_extra | 20 | m^2 |  | Cost_extra ($/m^2) | 150 |  | Cost/m^3 | 275 | Catchment area | 3350 | 2014 | 334308 | L
Catchment Area | 120 | m^2 | [6 empty] | Catchment Tank | 2000 | 2015 | 353544 | L
Storage Tank Volume | 27000 | L |  | 1% Satisfaction | 170 | L/day | Catchment Tank Costs |  | Storage Tank | 7425 | Average | 343926 | L
Catchment Tank Volume | 10000 | L |  | 50% Satisfaction | 368 | L/day | Volume | $ | Storage Tower | 0
Cmin | 136 | L/day |  | 100% Satisfaction | 581 | L/day | 400 | 200 | Total | 12775
Cmax | 601 | L/day |  |  |  |  | 1500 | 500
Consumption | 600 | L/day |  |  |  |  | 2500 | 900
Vinitial | 0 | L |  |  |  |  | 10000 | 2000
Time | 1 | day
Reliability -2014 | 333 | days/year
Reliability -2015 | 312 | days/year
Station 1-2014 Data | [13 empty] | Station 1-2015 Data
Date | Daily Rainfall (mm) | Qin(L/day) | Qout (L/day) | Volume in Storage (L) | Satisfaction | [8 empty] | Date | Daily Rainfall (mm) | Qin(L/day) | Qout (L/day) | Volume in Storage (L) | Satisfaction
1/1/2014 | 18.8 | 2256 | 0 | 2256 | 19.66% | [8 empty] | 1/1/2015 | 7.8 | 936 | 0 | 936 | 19.66%
1/2/2014 | 19.8 | 2376 | 0 | 4632 | 19.66% | [8 empty] | 1/2/2015 | 1 | 120 | 0 | 1056 | 19.66%
1/3/2014 | 0 | 0 | 0 | 4632 | 19.66% | [8 empty] | 1/3/2015 | 13.4 | 1608 | 0 | 2664 | 19.66%
1/4/2014 | 0 | 0 | 0 | 4632 | 19.66% | [8 empty] | 1/4/2015 | 64.2 | 7704 | 0 | 10368 | 19.66%
1/5/2014 | 0 | 0 | 0 | 4632 | 19.66% | [8 empty] | 1/5/2015 | 32.2 | 3864 | 0 | 14232 | 19.66%
1/6/2014 | 5 | 600 | 0 | 5232 | 19.66% | [8 empty] | 1/6/2015 | 2.8 | 336 | 0 | 14568 | 19.66%
1/7/2014 | 20.4 | 2448 | 0 | 7680 | 19.66% | [8 empty] | 1/7/2015 | 0 | 0 | 0 | 14568 | 19.66%
1/8/2014 | 24.8 | 2976 | 0 | 10656 | 19.66% | [8 empty] | 1/8/2015 | 0 | 0 | 0 | 14568 | 19.66%
1/9/2014 | 34 | 4080 | 0 | 14736 | 19.66% | [8 empty] | 1/9/2015 | 0.8 | 96 | 0 | 14664 | 19.66%
1/10/2014 | 44.6 | 5352 | 0 | 20088 | 19.66% | [8 empty] | 1/10/2015 | 0 | 0 | 0 | 14664 | 19.66%
1/11/2014 | 14.4 | 1728 | 0 | 21816 | 19.66% | [8 empty] | 1/11/2015 | 0 | 0 | 0 | 14664 | 19.66%
1/12/2014 | 50.2 | 6024 | 0 | 27000 | 19.66% | [8 empty] | 1/12/2015 | 0 | 0 | 0 | 14664 | 19.66%
1/13/2014 | 9.6 | 1152 | 0 | 27000 | 19.66% | [8 empty] | 1/13/2015 | 0 | 0 | 0 | 14664 | 19.66%
1/14/2014 | 5.8 | 696 | 0 | 27000 | 19.66% | [8 empty] | 1/14/2015 | 0.4 | 48 | 0 | 14712 | 19.66%
1/15/2014 | 1.6 | 192 | 0 | 27000 | 19.66% | [8 empty] | 1/15/2015 | 35.4 | 4248 | 0 | 18960 | 19.66%
1/16/2014 | 0.8 | 96 | 0 | 27000 | 19.66% | [8 empty] | 1/16/2015 | 6 | 720 | 0 | 19680 | 19.66%
1/17/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/17/2015 | 20.4 | 2448 | 0 | 22128 | 19.66%
1/18/2014 | 2.6 | 312 | 0 | 27000 | 19.66% | [8 empty] | 1/18/2015 | 16.6 | 1992 | 0 | 24120 | 19.66%
1/19/2014 | 1 | 120 | 0 | 27000 | 19.66% | [8 empty] | 1/19/2015 | 2.6 | 312 | 0 | 24432 | 19.66%
1/20/2014 | 0.6 | 72 | 0 | 27000 | 19.66% | [8 empty] | 1/20/2015 | 0.4 | 48 | 0 | 24480 | 19.66%
1/21/2014 | 0.8 | 96 | 0 | 27000 | 19.66% | [8 empty] | 1/21/2015 | 18.4 | 2208 | 0 | 26688 | 19.66%
1/22/2014 | 0.6 | 72 | 0 | 27000 | 19.66% | [8 empty] | 1/22/2015 | 14 | 1680 | 0 | 27000 | 19.66%
1/23/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/23/2015 | 90.8 | 10000 | 0 | 27000 | 19.66%
1/24/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/24/2015 | 40 | 4800 | 0 | 27000 | 19.66%
1/25/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/25/2015 | 1.8 | 216 | 0 | 27000 | 19.66%
1/26/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/26/2015 | 2.8 | 336 | 0 | 27000 | 19.66%
1/27/2014 | 17.6 | 2112 | 0 | 27000 | 19.66% | [8 empty] | 1/27/2015 | 2.8 | 336 | 0 | 27000 | 19.66%
1/28/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/28/2015 | 0 | 0 | 0 | 27000 | 19.66%
1/29/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/29/2015 | 0 | 0 | 0 | 27000 | 19.66%
1/30/2014 | 0 | 0 | 0 | 27000 | 19.66% | [8 empty] | 1/30/2015 | 0.6 | 72 | 0 | 27000 | 19.66%
1/31/2014 | 2.6 | 312 | 0 | 27000 | 19.66% | [8 empty] | 1/31/2015 | 5.8 | 696 | 0 | 27000 | 19.66%
2/1/2014 | 2.6 | 312 | 600 | 26712 | 100% | [8 empty] | 2/1/2015 | 8 | 960 | 600 | 27000 | 100%
2/2/2014 | 0 | 0 | 600 | 26112 | 100% | [8 empty] | 2/2/2015 | 27 | 3240 | 600 | 27000 | 100%
2/3/2014 | 0 | 0 | 600 | 25512 | 100% | [8 empty] | 2/3/2015 | 0.6 | 72 | 600 | 26472 | 100%
2/4/2014 | 0 | 0 | 600 | 24912 | 100% | [8 empty] | 2/4/2015 | 36 | 4320 | 600 | 27000 | 100%
2/5/2014 | 0 | 0 | 600 | 24312 | 100% | [8 empty] | 2/5/2015 | 27.2 | 3264 | 600 | 27000 | 100%
2/6/2014 | 0 | 0 | 600 | 23712 | 100% | [8 empty] | 2/6/2015 | 28.2 | 3384 | 600 | 27000 | 100%
2/7/2014 | 0 | 0 | 600 | 23112 | 100% | [8 empty] | 2/7/2015 | 39.2 | 4704 | 600 | 27000 | 100%
2/8/2014 | 0 | 0 | 600 | 22512 | 100% | [8 empty] | 2/8/2015 | 6.6 | 792 | 600 | 27000 | 100%
2/9/2014 | 12.2 | 1464 | 600 | 23376 | 100% | [8 empty] | 2/9/2015 | 3.2 | 384 | 600 | 26784 | 100%
2/10/2014 | 13.4 | 1608 | 600 | 24384 | 100% | [8 empty] | 2/10/2015 | 0.2 | 24 | 600 | 26208 | 100%
2/11/2014 | 46.6 | 5592 | 600 | 27000 | 100% | [8 empty] | 2/11/2015 | 19.6 | 2352 | 600 | 27000 | 100%
2/12/2014 | 16.8 | 2016 | 600 | 27000 | 100% | [8 empty] | 2/12/2015 | 30.4 | 3648 | 600 | 27000 | 100%
2/13/2014 | 15.6 | 1872 | 600 | 27000 | 100% | [8 empty] | 2/13/2015 | 19 | 2280 | 600 | 27000 | 100%
2/14/2014 | 3 | 360 | 600 | 26760 | 100% | [8 empty] | 2/14/2015 | 0.2 | 24 | 600 | 26424 | 100%
2/15/2014 | 11.6 | 1392 | 600 | 27000 | 100% | [8 empty] | 2/15/2015 | 0 | 0 | 600 | 25824 | 100%
2/16/2014 | 19 | 2280 | 600 | 27000 | 100% | [8 empty] | 2/16/2015 | 0 | 0 | 600 | 25224 | 100%
2/17/2014 | 9.2 | 1104 | 600 | 27000 | 100% | [8 empty] | 2/17/2015 | 0 | 0 | 600 | 24624 | 100%
2/18/2014 | 12.6 | 1512 | 600 | 27000 | 100% | [8 empty] | 2/18/2015 | 4 | 480 | 600 | 24504 | 100%
2/19/2014 | 21.8 | 2616 | 600 | 27000 | 100% | [8 empty] | 2/19/2015 | 11 | 1320 | 600 | 25224 | 100%
2/20/2014 | 2.4 | 288 | 600 | 26688 | 100% | [8 empty] | 2/20/2015 | 0.4 | 48 | 600 | 24672 | 100%
2/21/2014 | 0.8 | 96 | 600 | 26184 | 100% | [8 empty] | 2/21/2015 | 0 | 0 | 600 | 24072 | 100%
2/22/2014 | 4.8 | 576 | 600 | 26160 | 100% | [8 empty] | 2/22/2015 | 0 | 0 | 600 | 23472 | 100%
2/23/2014 | 14.6 | 1752 | 600 | 27000 | 100% | [8 empty] | 2/23/2015 | 0 | 0 | 600 | 22872 | 100%
2/24/2014 | 6.8 | 816 | 600 | 27000 | 100% | [8 empty] | 2/24/2015 | 0.2 | 24 | 600 | 22296 | 100%
2/25/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 2/25/2015 | 4.6 | 552 | 600 | 22248 | 100%
2/26/2014 | 0.8 | 96 | 600 | 25896 | 100% | [8 empty] | 2/26/2015 | 8.8 | 1056 | 600 | 22704 | 100%
2/27/2014 | 0 | 0 | 600 | 25296 | 100% | [8 empty] | 2/27/2015 | 0.4 | 48 | 600 | 22152 | 100%
2/28/2014 | 0.4 | 48 | 600 | 24744 | 100% | [8 empty] | 2/28/2015 | 0 | 0 | 600 | 21552 | 100%
3/1/2014 | 2 | 240 | 600 | 24384 | 100% | [8 empty] | 3/1/2015 | 1.2 | 144 | 600 | 21096 | 100%
3/2/2014 | 19 | 2280 | 600 | 26064 | 100% | [8 empty] | 3/2/2015 | 0 | 0 | 600 | 20496 | 100%
3/3/2014 | 1 | 120 | 600 | 25584 | 100% | [8 empty] | 3/3/2015 | 0 | 0 | 600 | 19896 | 100%
3/4/2014 | 2.4 | 288 | 600 | 25272 | 100% | [8 empty] | 3/4/2015 | 0.4 | 48 | 600 | 19344 | 100%
3/5/2014 | 23.8 | 2856 | 600 | 27000 | 100% | [8 empty] | 3/5/2015 | 1.8 | 216 | 600 | 18960 | 100%
3/6/2014 | 8.6 | 1032 | 600 | 27000 | 100% | [8 empty] | 3/6/2015 | 0.8 | 96 | 600 | 18456 | 100%
3/7/2014 | 34 | 4080 | 600 | 27000 | 100% | [8 empty] | 3/7/2015 | 0 | 0 | 600 | 17856 | 100%
3/8/2014 | 52.4 | 6288 | 600 | 27000 | 100% | [8 empty] | 3/8/2015 | 0.4 | 48 | 600 | 17304 | 100%
3/9/2014 | 10.6 | 1272 | 600 | 27000 | 100% | [8 empty] | 3/9/2015 | 0.4 | 48 | 600 | 16752 | 100%
3/10/2014 | 2.4 | 288 | 600 | 26688 | 100% | [8 empty] | 3/10/2015 | 2.8 | 336 | 600 | 16488 | 100%
3/11/2014 | 0 | 0 | 600 | 26088 | 100% | [8 empty] | 3/11/2015 | 13.6 | 1632 | 600 | 17520 | 100%
3/12/2014 | 2.8 | 336 | 600 | 25824 | 100% | [8 empty] | 3/12/2015 | 8.6 | 1032 | 600 | 17952 | 100%
3/13/2014 | 20.2 | 2424 | 600 | 27000 | 100% | [8 empty] | 3/13/2015 | 17.4 | 2088 | 600 | 19440 | 100%
3/14/2014 | 13.8 | 1656 | 600 | 27000 | 100% | [8 empty] | 3/14/2015 | 0.6 | 72 | 600 | 18912 | 100%
3/15/2014 | 22.8 | 2736 | 600 | 27000 | 100% | [8 empty] | 3/15/2015 | 0 | 0 | 600 | 18312 | 100%
3/16/2014 | 5.4 | 648 | 600 | 27000 | 100% | [8 empty] | 3/16/2015 | 0 | 0 | 600 | 17712 | 100%
3/17/2014 | 0.4 | 48 | 600 | 26448 | 100% | [8 empty] | 3/17/2015 | 0 | 0 | 600 | 17112 | 100%
3/18/2014 | 31 | 3720 | 600 | 27000 | 100% | [8 empty] | 3/18/2015 | 31 | 3720 | 600 | 20232 | 100%
3/19/2014 | 1.6 | 192 | 600 | 26592 | 100% | [8 empty] | 3/19/2015 | 35.4 | 4248 | 600 | 23880 | 100%
3/20/2014 | 1.6 | 192 | 600 | 26184 | 100% | [8 empty] | 3/20/2015 | 28.6 | 3432 | 600 | 26712 | 100%
3/21/2014 | 7.6 | 912 | 600 | 26496 | 100% | [8 empty] | 3/21/2015 | 0 | 0 | 600 | 26112 | 100%
3/22/2014 | 2.6 | 312 | 600 | 26208 | 100% | [8 empty] | 3/22/2015 | 7 | 840 | 600 | 26352 | 100%
3/23/2014 | 0 | 0 | 600 | 25608 | 100% | [8 empty] | 3/23/2015 | 9.6 | 1152 | 600 | 26904 | 100%
3/24/2014 | 4 | 480 | 600 | 25488 | 100% | [8 empty] | 3/24/2015 | 18.2 | 2184 | 600 | 27000 | 100%
3/25/2014 | 31 | 3720 | 600 | 27000 | 100% | [8 empty] | 3/25/2015 | 104.4 | 10000 | 600 | 27000 | 100%
3/26/2014 | 0.2 | 24 | 600 | 26424 | 100% | [8 empty] | 3/26/2015 | 33.2 | 3984 | 600 | 27000 | 100%
3/27/2014 | 4.4 | 528 | 600 | 26352 | 100% | [8 empty] | 3/27/2015 | 26.2 | 3144 | 600 | 27000 | 100%
3/28/2014 | 23.6 | 2832 | 600 | 27000 | 100% | [8 empty] | 3/28/2015 | 68.8 | 8256 | 600 | 27000 | 100%
3/29/2014 | 41.6 | 4992 | 600 | 27000 | 100% | [8 empty] | 3/29/2015 | 10 | 1200 | 600 | 27000 | 100%
3/30/2014 | 3 | 360 | 600 | 26760 | 100% | [8 empty] | 3/30/2015 | 37.7 | 4524 | 600 | 27000 | 100%
3/31/2014 | 0 | 0 | 600 | 26160 | 100% | [8 empty] | 3/31/2015 | 11.6 | 1392 | 600 | 27000 | 100%
4/1/2014 | 0 | 0 | 600 | 25560 | 100% | [8 empty] | 4/1/2015 | 0 | 0 | 600 | 26400 | 100%
4/2/2014 | 5.6 | 672 | 600 | 25632 | 100% | [8 empty] | 4/2/2015 | 33.7 | 4044 | 600 | 27000 | 100%
4/3/2014 | 20.4 | 2448 | 600 | 27000 | 100% | [8 empty] | 4/3/2015 | 9 | 1080 | 600 | 27000 | 100%
4/4/2014 | 2.6 | 312 | 600 | 26712 | 100% | [8 empty] | 4/4/2015 | 8.4 | 1008 | 600 | 27000 | 100%
4/5/2014 | 15.9 | 1908 | 600 | 27000 | 100% | [8 empty] | 4/5/2015 | 0.6 | 72 | 600 | 26472 | 100%
4/6/2014 | 9.4 | 1128 | 600 | 27000 | 100% | [8 empty] | 4/6/2015 | 0 | 0 | 600 | 25872 | 100%
4/7/2014 | 13.6 | 1632 | 600 | 27000 | 100% | [8 empty] | 4/7/2015 | 0 | 0 | 600 | 25272 | 100%
4/8/2014 | 5.6 | 672 | 600 | 27000 | 100% | [8 empty] | 4/8/2015 | 0 | 0 | 600 | 24672 | 100%
4/9/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 4/9/2015 | 3.2 | 384 | 600 | 24456 | 100%
4/10/2014 | 16.6 | 1992 | 600 | 27000 | 100% | [8 empty] | 4/10/2015 | 40.2 | 4824 | 600 | 27000 | 100%
4/11/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 4/11/2015 | 9.2 | 1104 | 600 | 27000 | 100%
4/12/2014 | 0 | 0 | 600 | 25800 | 100% | [8 empty] | 4/12/2015 | 24.4 | 2928 | 600 | 27000 | 100%
4/13/2014 | 0 | 0 | 600 | 25200 | 100% | [8 empty] | 4/13/2015 | 16.2 | 1944 | 600 | 27000 | 100%
4/14/2014 | 14.8 | 1776 | 600 | 26376 | 100% | [8 empty] | 4/14/2015 | 1.5 | 180 | 600 | 26580 | 100%
4/15/2014 | 20.8 | 2496 | 600 | 27000 | 100% | [8 empty] | 4/15/2015 | 37.2 | 4464 | 600 | 27000 | 100%
4/16/2014 | 37.4 | 4488 | 600 | 27000 | 100% | [8 empty] | 4/16/2015 | 3 | 360 | 600 | 26760 | 100%
4/17/2014 | 9.8 | 1176 | 600 | 27000 | 100% | [8 empty] | 4/17/2015 | 0 | 0 | 600 | 26160 | 100%
4/18/2014 | 1.9 | 228 | 600 | 26628 | 100% | [8 empty] | 4/18/2015 | 0 | 0 | 600 | 25560 | 100%
4/19/2014 | 21 | 2520 | 600 | 27000 | 100% | [8 empty] | 4/19/2015 | 0 | 0 | 600 | 24960 | 100%
4/20/2014 | 30 | 3600 | 600 | 27000 | 100% | [8 empty] | 4/20/2015 | 1.1 | 132 | 600 | 24492 | 100%
4/21/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 4/21/2015 | 0.4 | 48 | 600 | 23940 | 100%
4/22/2014 | 4.4 | 528 | 600 | 26328 | 100% | [8 empty] | 4/22/2015 | 8.2 | 984 | 600 | 24324 | 100%
4/23/2014 | 12.8 | 1536 | 600 | 27000 | 100% | [8 empty] | 4/23/2015 | 8.4 | 1008 | 600 | 24732 | 100%
4/24/2014 | 26 | 3120 | 600 | 27000 | 100% | [8 empty] | 4/24/2015 | 1.8 | 216 | 600 | 24348 | 100%
4/25/2014 | 1.8 | 216 | 600 | 26616 | 100% | [8 empty] | 4/25/2015 | 0 | 0 | 600 | 23748 | 100%
4/26/2014 | 35 | 4200 | 600 | 27000 | 100% | [8 empty] | 4/26/2015 | 4.2 | 504 | 600 | 23652 | 100%
4/27/2014 | 7.2 | 864 | 600 | 27000 | 100% | [8 empty] | 4/27/2015 | 22.4 | 2688 | 600 | 25740 | 100%
4/28/2014 | 0.8 | 96 | 600 | 26496 | 100% | [8 empty] | 4/28/2015 | 15.4 | 1848 | 600 | 26988 | 100%
4/29/2014 | 0.1 | 12 | 600 | 25908 | 100% | [8 empty] | 4/29/2015 | 27.6 | 3312 | 600 | 27000 | 100%
4/30/2014 | 0 | 0 | 600 | 25308 | 100% | [8 empty] | 4/30/2015 | 4.8 | 576 | 600 | 26976 | 100%
5/1/2014 | 0 | 0 | 600 | 24708 | 100% | [8 empty] | 5/1/2015 | 0.8 | 96 | 600 | 26472 | 100%
5/2/2014 | 2 | 240 | 600 | 24348 | 100% | [8 empty] | 5/2/2015 | 0 | 0 | 600 | 25872 | 100%
5/3/2014 | 4.6 | 552 | 600 | 24300 | 100% | [8 empty] | 5/3/2015 | 0 | 0 | 600 | 25272 | 100%
5/4/2014 | 3.8 | 456 | 600 | 24156 | 100% | [8 empty] | 5/4/2015 | 19.8 | 2376 | 600 | 27000 | 100%
5/5/2014 | 0 | 0 | 600 | 23556 | 100% | [8 empty] | 5/5/2015 | 0.4 | 48 | 600 | 26448 | 100%
5/6/2014 | 0 | 0 | 600 | 22956 | 100% | [8 empty] | 5/6/2015 | 0 | 0 | 600 | 25848 | 100%
5/7/2014 | 0 | 0 | 600 | 22356 | 100% | [8 empty] | 5/7/2015 | 0 | 0 | 600 | 25248 | 100%
5/8/2014 | 0 | 0 | 600 | 21756 | 100% | [8 empty] | 5/8/2015 | 0 | 0 | 600 | 24648 | 100%
5/9/2014 | 0 | 0 | 600 | 21156 | 100% | [8 empty] | 5/9/2015 | 0 | 0 | 600 | 24048 | 100%
5/10/2014 | 0.2 | 24 | 600 | 20580 | 100% | [8 empty] | 5/10/2015 | 0.4 | 48 | 600 | 23496 | 100%
5/11/2014 | 0 | 0 | 600 | 19980 | 100% | [8 empty] | 5/11/2015 | 0 | 0 | 600 | 22896 | 100%
5/12/2014 | 0.2 | 24 | 600 | 19404 | 100% | [8 empty] | 5/12/2015 | 0 | 0 | 600 | 22296 | 100%
5/13/2014 | 0 | 0 | 600 | 18804 | 100% | [8 empty] | 5/13/2015 | 0 | 0 | 600 | 21696 | 100%
5/14/2014 | 0 | 0 | 600 | 18204 | 100% | [8 empty] | 5/14/2015 | 0 | 0 | 600 | 21096 | 100%
5/15/2014 | 0 | 0 | 600 | 17604 | 100% | [8 empty] | 5/15/2015 | 0 | 0 | 600 | 20496 | 100%
5/16/2014 | 2.8 | 336 | 600 | 17340 | 100% | [8 empty] | 5/16/2015 | 0.2 | 24 | 600 | 19920 | 100%
5/17/2014 | 0 | 0 | 600 | 16740 | 100% | [8 empty] | 5/17/2015 | 0 | 0 | 600 | 19320 | 100%
5/18/2014 | 0 | 0 | 600 | 16140 | 100% | [8 empty] | 5/18/2015 | 0 | 0 | 600 | 18720 | 100%
5/19/2014 | 0 | 0 | 600 | 15540 | 100% | [8 empty] | 5/19/2015 | 0 | 0 | 600 | 18120 | 100%
5/20/2014 | 0 | 0 | 600 | 14940 | 100% | [8 empty] | 5/20/2015 | 0 | 0 | 600 | 17520 | 100%
5/21/2014 | 8.2 | 984 | 600 | 15324 | 100% | [8 empty] | 5/21/2015 | 0 | 0 | 600 | 16920 | 100%
5/22/2014 | 29.6 | 3552 | 600 | 18276 | 100% | [8 empty] | 5/22/2015 | 0.2 | 24 | 600 | 16344 | 100%
5/23/2014 | 0.8 | 96 | 600 | 17772 | 100% | [8 empty] | 5/23/2015 | 0.2 | 24 | 600 | 15768 | 100%
5/24/2014 | 5.2 | 624 | 600 | 17796 | 100% | [8 empty] | 5/24/2015 | 0 | 0 | 600 | 15168 | 100%
5/25/2014 | 23.4 | 2808 | 600 | 20004 | 100% | [8 empty] | 5/25/2015 | 0 | 0 | 600 | 14568 | 100%
5/26/2014 | 0 | 0 | 600 | 19404 | 100% | [8 empty] | 5/26/2015 | 0 | 0 | 600 | 13968 | 100%
5/27/2014 | 4.4 | 528 | 600 | 19332 | 100% | [8 empty] | 5/27/2015 | 0 | 0 | 600 | 13368 | 100%
5/28/2014 | 0 | 0 | 600 | 18732 | 100% | [8 empty] | 5/28/2015 | 0 | 0 | 600 | 12768 | 100%
5/29/2014 | 0 | 0 | 600 | 18132 | 100% | [8 empty] | 5/29/2015 | 0 | 0 | 600 | 12168 | 100%
5/30/2014 | 0 | 0 | 600 | 17532 | 100% | [8 empty] | 5/30/2015 | 0 | 0 | 600 | 11568 | 100%
5/31/2014 | 0 | 0 | 600 | 16932 | 100% | [8 empty] | 5/31/2015 | 0 | 0 | 600 | 10968 | 100%
6/1/2014 | 0 | 0 | 600 | 16332 | 100% | [8 empty] | 6/1/2015 | 7.4 | 888 | 600 | 11256 | 100%
6/2/2014 | 0 | 0 | 600 | 15732 | 100% | [8 empty] | 6/2/2015 | 2.8 | 336 | 600 | 10992 | 100%
6/3/2014 | 0 | 0 | 600 | 15132 | 100% | [8 empty] | 6/3/2015 | 0 | 0 | 600 | 10392 | 100%
6/4/2014 | 0 | 0 | 600 | 14532 | 100% | [8 empty] | 6/4/2015 | 0 | 0 | 600 | 9792 | 100%
6/5/2014 | 0 | 0 | 600 | 13932 | 100% | [8 empty] | 6/5/2015 | 0 | 0 | 600 | 9192 | 100%
6/6/2014 | 0 | 0 | 600 | 13332 | 100% | [8 empty] | 6/6/2015 | 0 | 0 | 600 | 8592 | 100%
6/7/2014 | 0 | 0 | 600 | 12732 | 100% | [8 empty] | 6/7/2015 | 0 | 0 | 600 | 7992 | 100%
6/8/2014 | 0.2 | 24 | 600 | 12156 | 100% | [8 empty] | 6/8/2015 | 0 | 0 | 600 | 7392 | 100%
6/9/2014 | 0 | 0 | 600 | 11556 | 100% | [8 empty] | 6/9/2015 | 0 | 0 | 600 | 6792 | 100%
6/10/2014 | 0 | 0 | 600 | 10956 | 100% | [8 empty] | 6/10/2015 | 0 | 0 | 600 | 6192 | 100%
6/11/2014 | 0 | 0 | 600 | 10356 | 100% | [8 empty] | 6/11/2015 | 0 | 0 | 600 | 5592 | 100%
6/12/2014 | 0 | 0 | 600 | 9756 | 100% | [8 empty] | 6/12/2015 | 0 | 0 | 600 | 4992 | 100%
6/13/2014 | 0 | 0 | 600 | 9156 | 100% | [8 empty] | 6/13/2015 | 0 | 0 | 600 | 4392 | 100%
6/14/2014 | 3.6 | 432 | 600 | 8988 | 100% | [8 empty] | 6/14/2015 | 0 | 0 | 600 | 3792 | 100%
6/15/2014 | 0 | 0 | 600 | 8388 | 100% | [8 empty] | 6/15/2015 | 0 | 0 | 600 | 3192 | 100%
6/16/2014 | 0 | 0 | 600 | 7788 | 100% | [8 empty] | 6/16/2015 | 0 | 0 | 600 | 2592 | 100%
6/17/2014 | 0 | 0 | 600 | 7188 | 100% | [8 empty] | 6/17/2015 | 0 | 0 | 600 | 1992 | 100%
6/18/2014 | 1.6 | 192 | 600 | 6780 | 100% | [8 empty] | 6/18/2015 | 7 | 840 | 600 | 2232 | 100%
6/19/2014 | 20.8 | 2496 | 600 | 8676 | 100% | [8 empty] | 6/19/2015 | 0 | 0 | 600 | 1632 | 100%
6/20/2014 | 3.2 | 384 | 600 | 8460 | 100% | [8 empty] | 6/20/2015 | 0 | 0 | 600 | 1032 | 100%
6/21/2014 | 1.2 | 144 | 600 | 8004 | 100% | [8 empty] | 6/21/2015 | 0 | 0 | 600 | 432 | 100%
6/22/2014 | 0 | 0 | 600 | 7404 | 100% | [8 empty] | 6/22/2015 | 0 | 0 | 600 | 0 | 100%
6/23/2014 | 15.4 | 1848 | 600 | 8652 | 100% | [8 empty] | 6/23/2015 | 1.4 | 168 | 600 | 0 | 100%
6/24/2014 | 1.2 | 144 | 600 | 8196 | 100% | [8 empty] | 6/24/2015 | 13.4 | 1608 | 600 | 1008 | 100%
6/25/2014 | 0 | 0 | 600 | 7596 | 100% | [8 empty] | 6/25/2015 | 4 | 480 | 600 | 888 | 100%
6/26/2014 | 5.8 | 696 | 600 | 7692 | 100% | [8 empty] | 6/26/2015 | 0 | 0 | 600 | 288 | 100%
6/27/2014 | 20.4 | 2448 | 600 | 9540 | 100% | [8 empty] | 6/27/2015 | 0 | 0 | 600 | 0 | 100%
6/28/2014 | 20.4 | 2448 | 600 | 11388 | 100% | [8 empty] | 6/28/2015 | 0 | 0 | 600 | 0 | 100%
6/29/2014 | 0.6 | 72 | 600 | 10860 | 100% | [8 empty] | 6/29/2015 | 0 | 0 | 600 | 0 | 100%
6/30/2014 | 0 | 0 | 600 | 10260 | 100% | [8 empty] | 6/30/2015 | 0 | 0 | 600 | 0 | 100%
7/1/2014 | 0 | 0 | 600 | 9660 | 100% | [8 empty] | 7/1/2015 | 0 | 0 | 600 | 0 | 100%
7/2/2014 | 1.8 | 216 | 600 | 9276 | 100% | [8 empty] | 7/2/2015 | 0 | 0 | 600 | 0 | 100%
7/3/2014 | 6.2 | 744 | 600 | 9420 | 100% | [8 empty] | 7/3/2015 | 0 | 0 | 600 | 0 | 100%
7/4/2014 | 9.4 | 1128 | 600 | 9948 | 100% | [8 empty] | 7/4/2015 | 0 | 0 | 600 | 0 | 100%
7/5/2014 | 26.6 | 3192 | 600 | 12540 | 100% | [8 empty] | 7/5/2015 | 0 | 0 | 600 | 0 | 100%
7/6/2014 | 13.6 | 1632 | 600 | 13572 | 100% | [8 empty] | 7/6/2015 | 0 | 0 | 600 | 0 | 100%
7/7/2014 | 0 | 0 | 600 | 12972 | 100% | [8 empty] | 7/7/2015 | 0.2 | 24 | 600 | 0 | 100%
7/8/2014 | 0 | 0 | 600 | 12372 | 100% | [8 empty] | 7/8/2015 | 0 | 0 | 600 | 0 | 100%
7/9/2014 | 0 | 0 | 600 | 11772 | 100% | [8 empty] | 7/9/2015 | 1 | 120 | 600 | 0 | 100%
7/10/2014 | 0 | 0 | 600 | 11172 | 100% | [8 empty] | 7/10/2015 | 1.2 | 144 | 600 | 0 | 100%
7/11/2014 | 0 | 0 | 600 | 10572 | 100% | [8 empty] | 7/11/2015 | 2.4 | 288 | 600 | 0 | 100%
7/12/2014 | 0 | 0 | 600 | 9972 | 100% | [8 empty] | 7/12/2015 | 4 | 480 | 600 | 0 | 100%
7/13/2014 | 0 | 0 | 600 | 9372 | 100% | [8 empty] | 7/13/2015 | 0 | 0 | 600 | 0 | 100%
7/14/2014 | 0 | 0 | 600 | 8772 | 100% | [8 empty] | 7/14/2015 | 0 | 0 | 600 | 0 | 100%
7/15/2014 | 0 | 0 | 600 | 8172 | 100% | [8 empty] | 7/15/2015 | 0 | 0 | 600 | 0 | 100%
7/16/2014 | 0 | 0 | 600 | 7572 | 100% | [8 empty] | 7/16/2015 | 0 | 0 | 600 | 0 | 100%
7/17/2014 | 0 | 0 | 600 | 6972 | 100% | [8 empty] | 7/17/2015 | 0 | 0 | 600 | 0 | 100%
7/18/2014 | 37 | 4440 | 600 | 10812 | 100% | [8 empty] | 7/18/2015 | 0 | 0 | 600 | 0 | 100%
7/19/2014 | 1.8 | 216 | 600 | 10428 | 100% | [8 empty] | 7/19/2015 | 0 | 0 | 600 | 0 | 100%
7/20/2014 | 0 | 0 | 600 | 9828 | 100% | [8 empty] | 7/20/2015 | 0.6 | 72 | 600 | 0 | 100%
7/21/2014 | 0 | 0 | 600 | 9228 | 100% | [8 empty] | 7/21/2015 | 0 | 0 | 600 | 0 | 100%
7/22/2014 | 8 | 960 | 600 | 9588 | 100% | [8 empty] | 7/22/2015 | 0 | 0 | 600 | 0 | 100%
7/23/2014 | 18.2 | 2184 | 600 | 11172 | 100% | [8 empty] | 7/23/2015 | 8.4 | 1008 | 600 | 408 | 100%
7/24/2014 | 0.6 | 72 | 600 | 10644 | 100% | [8 empty] | 7/24/2015 | 4 | 480 | 600 | 288 | 100%
7/25/2014 | 0 | 0 | 600 | 10044 | 100% | [8 empty] | 7/25/2015 | 4.2 | 504 | 600 | 192 | 100%
7/26/2014 | 0 | 0 | 600 | 9444 | 100% | [8 empty] | 7/26/2015 | 0 | 0 | 600 | 0 | 100%
7/27/2014 | 0 | 0 | 600 | 8844 | 100% | [8 empty] | 7/27/2015 | 0 | 0 | 600 | 0 | 100%
7/28/2014 | 0 | 0 | 600 | 8244 | 100% | [8 empty] | 7/28/2015 | 0 | 0 | 600 | 0 | 100%
7/29/2014 | 0 | 0 | 600 | 7644 | 100% | [8 empty] | 7/29/2015 | 0 | 0 | 600 | 0 | 100%
7/30/2014 | 0 | 0 | 600 | 7044 | 100% | [8 empty] | 7/30/2015 | 0 | 0 | 600 | 0 | 100%
7/31/2014 | 0 | 0 | 600 | 6444 | 100% | [8 empty] | 7/31/2015 | 0 | 0 | 600 | 0 | 100%
8/1/2014 | 0 | 0 | 600 | 5844 | 100% | [8 empty] | 8/1/2015 | 0 | 0 | 600 | 0 | 100%
8/2/2014 | 0 | 0 | 600 | 5244 | 100% | [8 empty] | 8/2/2015 | 0 | 0 | 600 | 0 | 100%
8/3/2014 | 0 | 0 | 600 | 4644 | 100% | [8 empty] | 8/3/2015 | 0 | 0 | 600 | 0 | 100%
8/4/2014 | 0 | 0 | 600 | 4044 | 100% | [8 empty] | 8/4/2015 | 0 | 0 | 600 | 0 | 100%
8/5/2014 | 0 | 0 | 600 | 3444 | 100% | [8 empty] | 8/5/2015 | 0 | 0 | 600 | 0 | 100%
8/6/2014 | 0 | 0 | 600 | 2844 | 100% | [8 empty] | 8/6/2015 | 3.2 | 384 | 600 | 0 | 100%
8/7/2014 | 0 | 0 | 600 | 2244 | 100% | [8 empty] | 8/7/2015 | 14.6 | 1752 | 600 | 1152 | 100%
8/8/2014 | 0 | 0 | 600 | 1644 | 100% | [8 empty] | 8/8/2015 | 24.4 | 2928 | 600 | 3480 | 100%
8/9/2014 | 0 | 0 | 600 | 1044 | 100% | [8 empty] | 8/9/2015 | 1.8 | 216 | 600 | 3096 | 100%
8/10/2014 | 0 | 0 | 600 | 444 | 100% | [8 empty] | 8/10/2015 | 0 | 0 | 600 | 2496 | 100%
8/11/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/11/2015 | 0 | 0 | 600 | 1896 | 100%
8/12/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/12/2015 | 0 | 0 | 600 | 1296 | 100%
8/13/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/13/2015 | 0 | 0 | 600 | 696 | 100%
8/14/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/14/2015 | 0 | 0 | 600 | 96 | 100%
8/15/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/15/2015 | 0 | 0 | 600 | 0 | 100%
8/16/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/16/2015 | 0 | 0 | 600 | 0 | 100%
8/17/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/17/2015 | 0 | 0 | 600 | 0 | 100%
8/18/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/18/2015 | 0 | 0 | 600 | 0 | 100%
8/19/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/19/2015 | 0 | 0 | 600 | 0 | 100%
8/20/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/20/2015 | 0 | 0 | 600 | 0 | 100%
8/21/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/21/2015 | 0 | 0 | 600 | 0 | 100%
8/22/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/22/2015 | 0 | 0 | 600 | 0 | 100%
8/23/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/23/2015 | 0 | 0 | 600 | 0 | 100%
8/24/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/24/2015 | 0 | 0 | 600 | 0 | 100%
8/25/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/25/2015 | 0 | 0 | 600 | 0 | 100%
8/26/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/26/2015 | 0 | 0 | 600 | 0 | 100%
8/27/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 8/27/2015 | 2.8 | 336 | 600 | 0 | 100%
8/28/2014 | 0.4 | 48 | 600 | 0 | 100% | [8 empty] | 8/28/2015 | 10.4 | 1248 | 600 | 648 | 100%
8/29/2014 | 7.8 | 936 | 600 | 336 | 100% | [8 empty] | 8/29/2015 | 33.4 | 4008 | 600 | 4056 | 100%
8/30/2014 | 3.6 | 432 | 600 | 168 | 100% | [8 empty] | 8/30/2015 | 26 | 3120 | 600 | 6576 | 100%
8/31/2014 | 10.6 | 1272 | 600 | 840 | 100% | [8 empty] | 8/31/2015 | 6 | 720 | 600 | 6696 | 100%
9/1/2014 | 3.2 | 384 | 600 | 624 | 100% | [8 empty] | 9/1/2015 | 15.8 | 1896 | 600 | 7992 | 100%
9/2/2014 | 6.2 | 744 | 600 | 768 | 100% | [8 empty] | 9/2/2015 | 0.8 | 96 | 600 | 7488 | 100%
9/3/2014 | 0 | 0 | 600 | 168 | 100% | [8 empty] | 9/3/2015 | 2.4 | 288 | 600 | 7176 | 100%
9/4/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/4/2015 | 0 | 0 | 600 | 6576 | 100%
9/5/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/5/2015 | 1.6 | 192 | 600 | 6168 | 100%
9/6/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/6/2015 | 0 | 0 | 600 | 5568 | 100%
9/7/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/7/2015 | 29.6 | 3552 | 600 | 8520 | 100%
9/8/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/8/2015 | 13 | 1560 | 600 | 9480 | 100%
9/9/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/9/2015 | 1.4 | 168 | 600 | 9048 | 100%
9/10/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/10/2015 | 0 | 0 | 600 | 8448 | 100%
9/11/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/11/2015 | 0 | 0 | 600 | 7848 | 100%
9/12/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/12/2015 | 0 | 0 | 600 | 7248 | 100%
9/13/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/13/2015 | 0 | 0 | 600 | 6648 | 100%
9/14/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/14/2015 | 0 | 0 | 600 | 6048 | 100%
9/15/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/15/2015 | 2 | 240 | 600 | 5688 | 100%
9/16/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/16/2015 | 4 | 480 | 600 | 5568 | 100%
9/17/2014 | 0 | 0 | 600 | 0 | 100% | [8 empty] | 9/17/2015 | 2.8 | 336 | 600 | 5304 | 100%
9/18/2014 | 26.4 | 3168 | 600 | 2568 | 100% | [8 empty] | 9/18/2015 | 46.4 | 5568 | 600 | 10272 | 100%
9/19/2014 | 0.4 | 48 | 600 | 2016 | 100% | [8 empty] | 9/19/2015 | 86.8 | 10000 | 600 | 19672 | 100%
9/20/2014 | 0 | 0 | 600 | 1416 | 100% | [8 empty] | 9/20/2015 | 1.4 | 168 | 600 | 19240 | 100%
9/21/2014 | 2 | 240 | 600 | 1056 | 100% | [8 empty] | 9/21/2015 | 4.2 | 504 | 600 | 19144 | 100%
9/22/2014 | 12.4 | 1488 | 600 | 1944 | 100% | [8 empty] | 9/22/2015 | 39.8 | 4776 | 600 | 23320 | 100%
9/23/2014 | 29.4 | 3528 | 600 | 4872 | 100% | [8 empty] | 9/23/2015 | 29.8 | 3576 | 600 | 26296 | 100%
9/24/2014 | 1.6 | 192 | 600 | 4464 | 100% | [8 empty] | 9/24/2015 | 11.8 | 1416 | 600 | 27000 | 100%
9/25/2014 | 0.6 | 72 | 600 | 3936 | 100% | [8 empty] | 9/25/2015 | 1.6 | 192 | 600 | 26592 | 100%
9/26/2014 | 8.2 | 984 | 600 | 4320 | 100% | [8 empty] | 9/26/2015 | 0 | 0 | 600 | 25992 | 100%
9/27/2014 | 0 | 0 | 600 | 3720 | 100% | [8 empty] | 9/27/2015 | 0 | 0 | 600 | 25392 | 100%
9/28/2014 | 12.4 | 1488 | 600 | 4608 | 100% | [8 empty] | 9/28/2015 | 0 | 0 | 600 | 24792 | 100%
9/29/2014 | 5.6 | 672 | 600 | 4680 | 100% | [8 empty] | 9/29/2015 | 0 | 0 | 600 | 24192 | 100%
9/30/2014 | 0 | 0 | 600 | 4080 | 100% | [8 empty] | 9/30/2015 | 0 | 0 | 600 | 23592 | 100%
10/1/2014 | 0 | 0 | 600 | 3480 | 100% | [8 empty] | 10/1/2015 | 0 | 0 | 600 | 22992 | 100%
10/2/2014 | 0 | 0 | 600 | 2880 | 100% | [8 empty] | 10/2/2015 | 0 | 0 | 600 | 22392 | 100%
10/3/2014 | 57.8 | 6936 | 600 | 9216 | 100% | [8 empty] | 10/3/2015 | 0 | 0 | 600 | 21792 | 100%
10/4/2014 | 6 | 720 | 600 | 9336 | 100% | [8 empty] | 10/4/2015 | 0 | 0 | 600 | 21192 | 100%
10/5/2014 | 9.2 | 1104 | 600 | 9840 | 100% | [8 empty] | 10/5/2015 | 0 | 0 | 600 | 20592 | 100%
10/6/2014 | 0.4 | 48 | 600 | 9288 | 100% | [8 empty] | 10/6/2015 | 4 | 480 | 600 | 20472 | 100%
10/7/2014 | 0 | 0 | 600 | 8688 | 100% | [8 empty] | 10/7/2015 | 15.6 | 1872 | 600 | 21744 | 100%
10/8/2014 | 1.4 | 168 | 600 | 8256 | 100% | [8 empty] | 10/8/2015 | 9.2 | 1104 | 600 | 22248 | 100%
10/9/2014 | 1.8 | 216 | 600 | 7872 | 100% | [8 empty] | 10/9/2015 | 26.4 | 3168 | 600 | 24816 | 100%
10/10/2014 | 17.8 | 2136 | 600 | 9408 | 100% | [8 empty] | 10/10/2015 | 27 | 3240 | 600 | 27000 | 100%
10/11/2014 | 15.4 | 1848 | 600 | 10656 | 100% | [8 empty] | 10/11/2015 | 37.6 | 4512 | 600 | 27000 | 100%
10/12/2014 | 33 | 3960 | 600 | 14016 | 100% | [8 empty] | 10/12/2015 | 0.8 | 96 | 600 | 26496 | 100%
10/13/2014 | 31.4 | 3768 | 600 | 17184 | 100% | [8 empty] | 10/13/2015 | 0.6 | 72 | 600 | 25968 | 100%
10/14/2014 | 28.4 | 3408 | 600 | 19992 | 100% | [8 empty] | 10/14/2015 | 0 | 0 | 600 | 25368 | 100%
10/15/2014 | 6.4 | 768 | 600 | 20160 | 100% | [8 empty] | 10/15/2015 | 0 | 0 | 600 | 24768 | 100%
10/16/2014 | 17.2 | 2064 | 600 | 21624 | 100% | [8 empty] | 10/16/2015 | 14.2 | 1704 | 600 | 25872 | 100%
10/17/2014 | 27 | 3240 | 600 | 24264 | 100% | [8 empty] | 10/17/2015 | 6.4 | 768 | 600 | 26040 | 100%
10/18/2014 | 16.8 | 2016 | 600 | 25680 | 100% | [8 empty] | 10/18/2015 | 23.4 | 2808 | 600 | 27000 | 100%
10/19/2014 | 46.2 | 5544 | 600 | 27000 | 100% | [8 empty] | 10/19/2015 | 0.6 | 72 | 600 | 26472 | 100%
10/20/2014 | 10.8 | 1296 | 600 | 27000 | 100% | [8 empty] | 10/20/2015 | 10.2 | 1224 | 600 | 27000 | 100%
10/21/2014 | 40.2 | 4824 | 600 | 27000 | 100% | [8 empty] | 10/21/2015 | 4 | 480 | 600 | 26880 | 100%
10/22/2014 | 21.4 | 2568 | 600 | 27000 | 100% | [8 empty] | 10/22/2015 | 9.8 | 1176 | 600 | 27000 | 100%
10/23/2014 | 9.4 | 1128 | 600 | 27000 | 100% | [8 empty] | 10/23/2015 | 0 | 0 | 600 | 26400 | 100%
10/24/2014 | 1.6 | 192 | 600 | 26592 | 100% | [8 empty] | 10/24/2015 | 5.8 | 696 | 600 | 26496 | 100%
10/25/2014 | 21.8 | 2616 | 600 | 27000 | 100% | [8 empty] | 10/25/2015 | 4 | 480 | 600 | 26376 | 100%
10/26/2014 | 2.4 | 288 | 600 | 26688 | 100% | [8 empty] | 10/26/2015 | 0 | 0 | 600 | 25776 | 100%
10/27/2014 | 33.6 | 4032 | 600 | 27000 | 100% | [8 empty] | 10/27/2015 | 6.8 | 816 | 600 | 25992 | 100%
10/28/2014 | 24.4 | 2928 | 600 | 27000 | 100% | [8 empty] | 10/28/2015 | 39 | 4680 | 600 | 27000 | 100%
10/29/2014 | 7 | 840 | 600 | 27000 | 100% | [8 empty] | 10/29/2015 | 40.6 | 4872 | 600 | 27000 | 100%
10/30/2014 | 9 | 1080 | 600 | 27000 | 100% | [8 empty] | 10/30/2015 | 35.4 | 4248 | 600 | 27000 | 100%
10/31/2014 | 15 | 1800 | 600 | 27000 | 100% | [8 empty] | 10/31/2015 | 21.2 | 2544 | 600 | 27000 | 100%
11/1/2014 | 6.4 | 768 | 600 | 27000 | 100% | [8 empty] | 11/1/2015 | 1.2 | 144 | 600 | 26544 | 100%
11/2/2014 | 37.6 | 4512 | 600 | 27000 | 100% | [8 empty] | 11/2/2015 | 0 | 0 | 600 | 25944 | 100%
11/3/2014 | 35.2 | 4224 | 600 | 27000 | 100% | [8 empty] | 11/3/2015 | 0 | 0 | 600 | 25344 | 100%
11/4/2014 | 9 | 1080 | 600 | 27000 | 100% | [8 empty] | 11/4/2015 | 3.4 | 408 | 600 | 25152 | 100%
11/5/2014 | 4.4 | 528 | 600 | 26928 | 100% | [8 empty] | 11/5/2015 | 6 | 720 | 600 | 25272 | 100%
11/6/2014 | 20.2 | 2424 | 600 | 27000 | 100% | [8 empty] | 11/6/2015 | 44.2 | 5304 | 600 | 27000 | 100%
11/7/2014 | 1.4 | 168 | 600 | 26568 | 100% | [8 empty] | 11/7/2015 | 2.2 | 264 | 600 | 26664 | 100%
11/8/2014 | 34 | 4080 | 600 | 27000 | 100% | [8 empty] | 11/8/2015 | 1.6 | 192 | 600 | 26256 | 100%
11/9/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 11/9/2015 | 0 | 0 | 600 | 25656 | 100%
11/10/2014 | 0 | 0 | 600 | 25800 | 100% | [8 empty] | 11/10/2015 | 20.5 | 2460 | 600 | 27000 | 100%
11/11/2014 | 0 | 0 | 600 | 25200 | 100% | [8 empty] | 11/11/2015 | 18.8 | 2256 | 600 | 27000 | 100%
11/12/2014 | 0 | 0 | 600 | 24600 | 100% | [8 empty] | 11/12/2015 | 59 | 7080 | 600 | 27000 | 100%
11/13/2014 | 0 | 0 | 600 | 24000 | 100% | [8 empty] | 11/13/2015 | 11.4 | 1368 | 600 | 27000 | 100%
11/14/2014 | 0 | 0 | 600 | 23400 | 100% | [8 empty] | 11/14/2015 | 0.6 | 72 | 600 | 26472 | 100%
11/15/2014 | 0 | 0 | 600 | 22800 | 100% | [8 empty] | 11/15/2015 | 6 | 720 | 600 | 26592 | 100%
11/16/2014 | 0 | 0 | 600 | 22200 | 100% | [8 empty] | 11/16/2015 | 55.4 | 6648 | 600 | 27000 | 100%
11/17/2014 | 0 | 0 | 600 | 21600 | 100% | [8 empty] | 11/17/2015 | 6.2 | 744 | 600 | 27000 | 100%
11/18/2014 | 0 | 0 | 600 | 21000 | 100% | [8 empty] | 11/18/2015 | 0 | 0 | 600 | 26400 | 100%
11/19/2014 | 3.4 | 408 | 600 | 20808 | 100% | [8 empty] | 11/19/2015 | 0 | 0 | 600 | 25800 | 100%
11/20/2014 | 29.4 | 3528 | 600 | 23736 | 100% | [8 empty] | 11/20/2015 | 0 | 0 | 600 | 25200 | 100%
11/21/2014 | 32.8 | 3936 | 600 | 27000 | 100% | [8 empty] | 11/21/2015 | 0 | 0 | 600 | 24600 | 100%
11/22/2014 | 25.6 | 3072 | 600 | 27000 | 100% | [8 empty] | 11/22/2015 | 0 | 0 | 600 | 24000 | 100%
11/23/2014 | 15.2 | 1824 | 600 | 27000 | 100% | [8 empty] | 11/23/2015 | 0 | 0 | 600 | 23400 | 100%
11/24/2014 | 60.6 | 7272 | 600 | 27000 | 100% | [8 empty] | 11/24/2015 | 0 | 0 | 600 | 22800 | 100%
11/25/2014 | 15 | 1800 | 600 | 27000 | 100% | [8 empty] | 11/25/2015 | 0 | 0 | 600 | 22200 | 100%
11/26/2014 | 43 | 5160 | 600 | 27000 | 100% | [8 empty] | 11/26/2015 | 0 | 0 | 600 | 21600 | 100%
11/27/2014 | 15 | 1800 | 600 | 27000 | 100% | [8 empty] | 11/27/2015 | 0 | 0 | 600 | 21000 | 100%
11/28/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 11/28/2015 | 0 | 0 | 600 | 20400 | 100%
11/29/2014 | 0 | 0 | 600 | 25800 | 100% | [8 empty] | 11/29/2015 | 0 | 0 | 600 | 19800 | 100%
11/30/2014 | 0 | 0 | 600 | 25200 | 100% | [8 empty] | 11/30/2015 | 13 | 1560 | 600 | 20760 | 100%
12/1/2014 | 0 | 0 | 600 | 24600 | 100% | [8 empty] | 12/1/2015 | 34.6 | 4152 | 600 | 24312 | 100%
12/2/2014 | 0 | 0 | 600 | 24000 | 100% | [8 empty] | 12/2/2015 | 27.4 | 3288 | 600 | 27000 | 100%
12/3/2014 | 0 | 0 | 600 | 23400 | 100% | [8 empty] | 12/3/2015 | 32.6 | 3912 | 600 | 27000 | 100%
12/4/2014 | 1.2 | 144 | 600 | 22944 | 100% | [8 empty] | 12/4/2015 | 27.2 | 3264 | 600 | 27000 | 100%
12/5/2014 | 45.4 | 5448 | 600 | 27000 | 100% | [8 empty] | 12/5/2015 | 33.8 | 4056 | 600 | 27000 | 100%
12/6/2014 | 0.8 | 96 | 600 | 26496 | 100% | [8 empty] | 12/6/2015 | 22.4 | 2688 | 600 | 27000 | 100%
12/7/2014 | 15.2 | 1824 | 600 | 27000 | 100% | [8 empty] | 12/7/2015 | 37.2 | 4464 | 600 | 27000 | 100%
12/8/2014 | 48.6 | 5832 | 600 | 27000 | 100% | [8 empty] | 12/8/2015 | 27 | 3240 | 600 | 27000 | 100%
12/9/2014 | 34.2 | 4104 | 600 | 27000 | 100% | [8 empty] | 12/9/2015 | 4.8 | 576 | 600 | 26976 | 100%
12/10/2014 | 4.4 | 528 | 600 | 26928 | 100% | [8 empty] | 12/10/2015 | 12.2 | 1464 | 600 | 27000 | 100%
12/11/2014 | 17.8 | 2136 | 600 | 27000 | 100% | [8 empty] | 12/11/2015 | 3.4 | 408 | 600 | 26808 | 100%
12/12/2014 | 1.4 | 168 | 600 | 26568 | 100% | [8 empty] | 12/12/2015 | 23.8 | 2856 | 600 | 27000 | 100%
12/13/2014 | 1 | 120 | 600 | 26088 | 100% | [8 empty] | 12/13/2015 | 0 | 0 | 600 | 26400 | 100%
12/14/2014 | 0 | 0 | 600 | 25488 | 100% | [8 empty] | 12/14/2015 | 2.4 | 288 | 600 | 26088 | 100%
12/15/2014 | 9 | 1080 | 600 | 25968 | 100% | [8 empty] | 12/15/2015 | 3 | 360 | 600 | 25848 | 100%
12/16/2014 | 20.2 | 2424 | 600 | 27000 | 100% | [8 empty] | 12/16/2015 | 2.2 | 264 | 600 | 25512 | 100%
12/17/2014 | 0.8 | 96 | 600 | 26496 | 100% | [8 empty] | 12/17/2015 | 21.8 | 2616 | 600 | 27000 | 100%
12/18/2014 | 24.6 | 2952 | 600 | 27000 | 100% | [8 empty] | 12/18/2015 | 25.5 | 3060 | 600 | 27000 | 100%
12/19/2014 | 0 | 0 | 600 | 26400 | 100% | [8 empty] | 12/19/2015 | 31.8 | 3816 | 600 | 27000 | 100%
12/20/2014 | 0 | 0 | 600 | 25800 | 100% | [8 empty] | 12/20/2015 | 22.6 | 2712 | 600 | 27000 | 100%
12/21/2014 | 8.8 | 1056 | 600 | 26256 | 100% | [8 empty] | 12/21/2015 | 9 | 1080 | 600 | 27000 | 100%
12/22/2014 | 11.6 | 1392 | 600 | 27000 | 100% | [8 empty] | 12/22/2015 | 35.8 | 4296 | 600 | 27000 | 100%
12/23/2014 | 10 | 1200 | 600 | 27000 | 100% | [8 empty] | 12/23/2015 | 9.4 | 1128 | 600 | 27000 | 100%
12/24/2014 | 2.2 | 264 | 600 | 26664 | 100% | [8 empty] | 12/24/2015 | 0 | 0 | 600 | 26400 | 100%
12/25/2014 | 0.6 | 72 | 600 | 26136 | 100% | [8 empty] | 12/25/2015 | 0 | 0 | 600 | 25800 | 100%
12/26/2014 | 10.2 | 1224 | 600 | 26760 | 100% | [8 empty] | 12/26/2015 | 26.2 | 3144 | 600 | 27000 | 100%
12/27/2014 | 5.4 | 648 | 600 | 26808 | 100% | [8 empty] | 12/27/2015 | 1.6 | 192 | 600 | 26592 | 100%
12/28/2014 | 0 | 0 | 600 | 26208 | 100% | [8 empty] | 12/28/2015 | 0.2 | 24 | 600 | 26016 | 100%
12/29/2014 | 0 | 0 | 600 | 25608 | 100% | [8 empty] | 12/29/2015 | 0 | 0 | 600 | 25416 | 100%
12/30/2014 | 0 | 0 | 600 | 25008 | 100% | [8 empty] | 12/30/2015 | 0 | 0 | 600 | 24816 | 100%
12/31/2014 | 0 | 0 | 600 | 24408 | 100% | [8 empty] | 12/31/2015 | 0 | 0 | 600 | 24216 | 100%

## Filters
Parameters | Value | units | [5 empty] | Initial cost | Replacement cost
Cf | 3893.237 | [6 empty] | [$] | [$]
Consumption | 600 | L/day |  |  |  |  | 1um Filter | 125 | 75
[7 empty] | 5um Filter | 110 | 60
[7 empty] | 200um Filter | 100 | 50
Filter Modules
Filter Size | Present? | Cf | Actual Filter Life | No pre-FIlter | 5 um pre | 200 um pre
1um | y | 3798.28 | 20000 | 5000 | 20000 | 15000
5um |  | 1899.14 | 20000 | 10000 |  | 20000
200um | y | 94.957 | 20000 | 20000
TOTAL |  | 3893.237
Filter Replacements (USED IN COST SECTION) |  |  |  |  | Cost (5 years)
Filter Size | Filter Life | Replacement per 5 years | Replacements per year |  | Initial | 225
1um | 20000 | 54 | 10.8 |  | Replacement | 6750
5um | 20000 | 54 | 10.8 |  | Total | 6975
200um | 20000 | 54 | 10.8
| Combined | 108 | 21.6

## Pumps
Parameters | Value | units |  | Pump Coefficients |  |  | Specs |  | Usage
Storage Tank Height | 11.5 | m |  | a | -0.0191 |  | Cost of 1 pump | 580 | # of Maintenances / 5 years | 1
Distance to Storage Tank | 25.4951 | m |  | b | -0.4006 |  | MTBF (hr) | 1000 | 5 Years Cost | 1160
Pipe Diameter | 0.02 | m |  | c | 167.7 |  | Efficiency | 70%
Pipe Area | 0.00031416 | m^2 |  |  |  |  | Running hours / year (using avg of 2014 and 2015) | 304.7602 | Running hours / year (for max consumption) | 194.0606
Pipe Friction Factor | 0.05 | [7 empty] | # of Maintenances / 5 years (for pump with least MTBF) | 0
Loss Coeff | 10 |  |  | A | B | C |  |  | Thus, pump maintence a would always be 0
Cf | 3893.237 |  |  | -43655.2119 | -11444.3691 | 54885
Water density | 1000 | kg/m^3
Acceleration due to gravity | 9.81 | m/s^2
ρgh | 112815 | Pa
v (m/s) | Q (L/min) | System Curve (Pa) | Pump | Intercepts
0 | 0 | 112815 | 167700 | v | 0.99783
0.05 | 0.94248 | 113101.834 | 167305.4775 | Q | 18.8086
0.1 | 1.885 | 113573.0124 | 166877.0234 | p_up | 153408.4392
0.15 | 2.8274 | 114228.5352 | 166414.6375
0.2 | 3.7699 | 115068.4023 | 165918.32
0.25 | 4.7124 | 116092.6137 | 165388.0707
0.3 | 5.6549 | 117301.1696 | 164823.8898
0.35 | 6.5973 | 118694.0698 | 164225.7771
0.4 | 7.5398 | 120271.3143 | 163593.7328
0.45 | 8.4823 | 122032.9032 | 162927.7567
0.5 | 9.4248 | 123978.8365 | 162227.849
0.55 | 10.3673 | 126109.1141 | 161494.0095
0.6 | 11.3097 | 128423.7361 | 160726.2383
0.65 | 12.2522 | 130922.7025 | 159924.5355
0.7 | 13.1947 | 133606.0132 | 159088.9009
0.75 | 14.1372 | 136473.6682 | 158219.3347
0.8 | 15.0796 | 139525.6677 | 157315.8367
0.85 | 16.0221 | 142762.0114 | 156378.4071
0.9 | 16.9646 | 146182.6996 | 155407.0457
0.95 | 17.9071 | 149787.7321 | 154401.7527
1 | 18.8496 | 153577.109 | 153362.5279
1.05 | 19.792 | 157550.8302 | 152289.3715
1.1 | 20.7345 | 161708.8958 | 151182.2833
1.15 | 21.677 | 166051.3057 | 150041.2634
1.2 | 22.6195 | 170578.06 | 148866.3119
1.25 | 23.5619 | 175289.1587 | 147657.4286
1.3 | 24.5044 | 180184.6017 | 146414.6137
1.35 | 25.4469 | 185264.3891 | 145137.867
1.4 | 26.3894 | 190528.5208 | 143827.1887
1.45 | 27.3319 | 195976.9969 | 142482.5786
1.5 | 28.2743 | 201609.8174 | 141104.0369
1.55 | 29.2168 | 207426.9822 | 139691.5634
1.6 | 30.1593 | 213428.4914 | 138245.1583
1.65 | 31.1018 | 219614.345 | 136764.8214
1.7 | 32.0442 | 225984.5429 | 135250.5529
1.75 | 32.9867 | 232539.0851 | 133702.3526
1.8 | 33.9292 | 239277.9718 | 132120.2207
1.85 | 34.8717 | 246201.2027 | 130504.157
1.9 | 35.8142 | 253308.7781 | 128854.1616
1.95 | 36.7566 | 260600.6978 | 127170.2346
2 | 37.6991 | 268076.9618 | 125452.3758
2.05 | 38.6416 | 275737.5703 | 123700.5854
2.1 | 39.5841 | 283582.523 | 121914.8632
2.15 | 40.5265 | 291611.8202 | 120095.2094
2.2 | 41.469 | 299825.4617 | 118241.6238
2.25 | 42.4115 | 308223.4475 | 116354.1066
2.3 | 43.354 | 316805.7778 | 114432.6576
2.35 | 44.2965 | 325572.4523 | 112477.277
2.4 | 45.2389 | 334523.4713 | 110487.9646
2.45 | 46.1814 | 343658.8346 | 108464.7206
2.5 | 47.1239 | 352978.5422 | 106407.5448
2.55 | 48.0664 | 362482.5943 | 104316.4374
2.6 | 49.0088 | 372170.9906 | 102191.3982
2.65 | 49.9513 | 382043.7314 | 100032.4274
2.7 | 50.8938 | 392100.8165 | 97839.5248
2.75 | 51.8363 | 402342.2459 | 95612.6906
2.8 | 52.7788 | 412768.0198 | 93351.9246
2.85 | 53.7212 | 423378.1379 | 91057.2269
2.9 | 54.6637 | 434172.6005 | 88728.5976
2.95 | 55.6062 | 445151.4074 | 86366.0366
3 | 56.5487 | 456314.5586 | 83969.5438

## On Demand Flow Rate
Parameters | Value | units
Storage Tank Height | 10 | m
Distance to Storage Tank | 27.3861 | m
Pipe Diameter | 0.02 | m
Pipe Area | 0.00031416 | m^2
Pipe Friction Factor | 0.05
Loss Coeff | 10
Cf | 0
Water density | 1000 | kg/m^3
Acceleration due to gravity | 9.81 | m/s^2
ρgh | 98100 | Pa
QD | 29.8066 | L/min
v (m/s) | Q (L/min) | Pressure Loss (Pa) | Left Hand Side
0 | 0 | 0 |  | ρgh | 98100
0.05 | 0.94248 | 98.0816 | 0 | 98100 | 98100
0.1 | 1.885 | 392.3266 | 56.5487 | 98100 | 98100
0.15 | 2.8274 | 882.7348 | Intercept |  | 98100
0.2 | 3.7699 | 1569.3064 | v | 1.5813 | 98100
0.25 | 4.7124 | 2452.0412 | QD | 29.8066 | 98100
0.3 | 5.6549 | 3530.9394 |  |  | 98100
0.35 | 6.5973 | 4806.0008 |  |  | 98100
0.4 | 7.5398 | 6277.2256 |  |  | 98100
0.45 | 8.4823 | 7944.6136 |  |  | 98100
0.5 | 9.4248 | 9808.165 |  |  | 98100
0.55 | 10.3673 | 11867.8796 |  |  | 98100
0.6 | 11.3097 | 14123.7575 |  |  | 98100
0.65 | 12.2522 | 16575.7988 |  |  | 98100
0.7 | 13.1947 | 19224.0033 |  |  | 98100
0.75 | 14.1372 | 22068.3712 |  |  | 98100
0.8 | 15.0796 | 25108.9023 |  |  | 98100
0.85 | 16.0221 | 28345.5967 |  |  | 98100
0.9 | 16.9646 | 31778.4545 |  |  | 98100
0.95 | 17.9071 | 35407.4755 |  |  | 98100
1 | 18.8496 | 39232.6598 |  |  | 98100
1.05 | 19.792 | 43254.0075 |  |  | 98100
1.1 | 20.7345 | 47471.5184 |  |  | 98100
1.15 | 21.677 | 51885.1926 |  |  | 98100
1.2 | 22.6195 | 56495.0302 |  |  | 98100
1.25 | 23.5619 | 61301.031 |  |  | 98100
1.3 | 24.5044 | 66303.1951 |  |  | 98100
1.35 | 25.4469 | 71501.5226 |  |  | 98100
1.4 | 26.3894 | 76896.0133 |  |  | 98100
1.45 | 27.3319 | 82486.6673 |  |  | 98100
1.5 | 28.2743 | 88273.4846 |  |  | 98100
1.55 | 29.2168 | 94256.4653 |  |  | 98100
1.6 | 30.1593 | 100435.6092 |  |  | 98100
1.65 | 31.1018 | 106810.9164 |  |  | 98100
1.7 | 32.0442 | 113382.3869 |  |  | 98100
1.75 | 32.9867 | 120150.0208 |  |  | 98100
1.8 | 33.9292 | 127113.8179 |  |  | 98100
1.85 | 34.8717 | 134273.7783 |  |  | 98100
1.9 | 35.8142 | 141629.902 |  |  | 98100
1.95 | 36.7566 | 149182.1891 |  |  | 98100
2 | 37.6991 | 156930.6394 |  |  | 98100
2.05 | 38.6416 | 164875.253 |  |  | 98100
2.1 | 39.5841 | 173016.0299 |  |  | 98100
2.15 | 40.5265 | 181352.9701 |  |  | 98100
2.2 | 41.469 | 189886.0736 |  |  | 98100
2.25 | 42.4115 | 198615.3405 |  |  | 98100
2.3 | 43.354 | 207540.7706 |  |  | 98100
2.35 | 44.2965 | 216662.364 |  |  | 98100
2.4 | 45.2389 | 225980.1207 |  |  | 98100
2.45 | 46.1814 | 235494.0407 |  |  | 98100
2.5 | 47.1239 | 245204.124 |  |  | 98100
2.55 | 48.0664 | 255110.3706 |  |  | 98100
2.6 | 49.0088 | 265212.7805 |  |  | 98100
2.65 | 49.9513 | 275511.3538 |  |  | 98100
2.7 | 50.8938 | 286006.0903 |  |  | 98100
2.75 | 51.8363 | 296696.9901 |  |  | 98100
2.8 | 52.7788 | 307584.0532 |  |  | 98100
2.85 | 53.7212 | 318667.2796 |  |  | 98100
2.9 | 54.6637 | 329946.6693 |  |  | 98100
2.95 | 55.6062 | 341422.2223 |  |  | 98100
3 | 56.5487 | 353093.9386 |  |  | 98100

## Disinfection
| Value | Units |  | UV Specs |  |  |  | Chlorine Specs |  |  | Ozone Specs |  |  | Results (5 years)
Type | Chlorine |  |  | Cost | 500 | $ |  | Total Chlorine Required | 66861.6 | g | CtO3 | 50 | mg*min/L | Cost | 3100
UV Load | 36 | W |  | Bulb Cost | 90 | $ |  | Refill Operations 1 years (Maintenance) | 24 |  | EO3 | 2 | MJ/g03 | Maintenance | 120
Contact Time | 10 | mins |  | MTBF | 1 | year |  | Cost of Solution | 2400 | $ | Maintenance | 1 | Operation/Year
|  |  |  | Max Flow Rate | 25 | LPM |  | Initial Cost | 700 | $ | Initial Cost | 4000 | $
[8 empty] | Total cost (5 years) | 3100 | $
Station 1 - 2014 |  |  | Chlorine Disinfection |  |  | Ozone
Date | Daily Rainfall (mm) | Qin(L/day) | Mass of Chlorine Required (g) | Running Total (g) | Maintenance Operations | Mass of Ozone Required (g) | Energy Required (MJ)
1/1/2014 | 18.8 | 2256 | 451.2 | 451.2 |  | 0.078333 | 0.15667
1/2/2014 | 19.8 | 2376 | 475.2 | 926.4 |  | 0.0825 | 0.165
1/3/2014 | 0 | 0 | 0 | 926.4 |  | 0 | 0
1/4/2014 | 0 | 0 | 0 | 926.4 |  | 0 | 0
1/5/2014 | 0 | 0 | 0 | 926.4 |  | 0 | 0
1/6/2014 | 5 | 600 | 120 | 1046.4 |  | 0.020833 | 0.041667
1/7/2014 | 20.4 | 2448 | 489.6 | 1536 |  | 0.085 | 0.17
1/8/2014 | 24.8 | 2976 | 595.2 | 2131.2 |  | 0.10333 | 0.20667
1/9/2014 | 34 | 4080 | 816 | 2947.2 |  | 0.14167 | 0.28333
1/10/2014 | 44.6 | 5352 | 1070.4 | 1070.4 | 1 | 0.18583 | 0.37167
1/11/2014 | 14.4 | 1728 | 345.6 | 1416 |  | 0.06 | 0.12
1/12/2014 | 50.2 | 6024 | 1204.8 | 2620.8 |  | 0.20917 | 0.41833
1/13/2014 | 9.6 | 1152 | 230.4 | 2851.2 |  | 0.04 | 0.08
1/14/2014 | 5.8 | 696 | 139.2 | 2990.4 |  | 0.024167 | 0.048333
1/15/2014 | 1.6 | 192 | 38.4 | 38.4 | 1 | 0.0066667 | 0.013333
1/16/2014 | 0.8 | 96 | 19.2 | 57.6 |  | 0.0033333 | 0.0066667
1/17/2014 | 0 | 0 | 0 | 57.6 |  | 0 | 0
1/18/2014 | 2.6 | 312 | 62.4 | 120 |  | 0.010833 | 0.021667
1/19/2014 | 1 | 120 | 24 | 144 |  | 0.0041667 | 0.0083333
1/20/2014 | 0.6 | 72 | 14.4 | 158.4 |  | 0.0025 | 0.005
1/21/2014 | 0.8 | 96 | 19.2 | 177.6 |  | 0.0033333 | 0.0066667
1/22/2014 | 0.6 | 72 | 14.4 | 192 |  | 0.0025 | 0.005
1/23/2014 | 0 | 0 | 0 | 192 |  | 0 | 0
1/24/2014 | 0 | 0 | 0 | 192 |  | 0 | 0
1/25/2014 | 0 | 0 | 0 | 192 |  | 0 | 0
1/26/2014 | 0 | 0 | 0 | 192 |  | 0 | 0
1/27/2014 | 17.6 | 2112 | 422.4 | 614.4 |  | 0.073333 | 0.14667
1/28/2014 | 0 | 0 | 0 | 614.4 |  | 0 | 0
1/29/2014 | 0 | 0 | 0 | 614.4 |  | 0 | 0
1/30/2014 | 0 | 0 | 0 | 614.4 |  | 0 | 0
1/31/2014 | 2.6 | 312 | 62.4 | 676.8 |  | 0.010833 | 0.021667
2/1/2014 | 2.6 | 312 | 62.4 | 739.2 |  | 0.010833 | 0.021667
2/2/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/3/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/4/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/5/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/6/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/7/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/8/2014 | 0 | 0 | 0 | 739.2 |  | 0 | 0
2/9/2014 | 12.2 | 1464 | 292.8 | 1032 |  | 0.050833 | 0.10167
2/10/2014 | 13.4 | 1608 | 321.6 | 1353.6 |  | 0.055833 | 0.11167
2/11/2014 | 46.6 | 5592 | 1118.4 | 2472 |  | 0.19417 | 0.38833
2/12/2014 | 16.8 | 2016 | 403.2 | 2875.2 |  | 0.07 | 0.14
2/13/2014 | 15.6 | 1872 | 374.4 | 374.4 | 1 | 0.065 | 0.13
2/14/2014 | 3 | 360 | 72 | 446.4 |  | 0.0125 | 0.025
2/15/2014 | 11.6 | 1392 | 278.4 | 724.8 |  | 0.048333 | 0.096667
2/16/2014 | 19 | 2280 | 456 | 1180.8 |  | 0.079167 | 0.15833
2/17/2014 | 9.2 | 1104 | 220.8 | 1401.6 |  | 0.038333 | 0.076667
2/18/2014 | 12.6 | 1512 | 302.4 | 1704 |  | 0.0525 | 0.105
2/19/2014 | 21.8 | 2616 | 523.2 | 2227.2 |  | 0.090833 | 0.18167
2/20/2014 | 2.4 | 288 | 57.6 | 2284.8 |  | 0.01 | 0.02
2/21/2014 | 0.8 | 96 | 19.2 | 2304 |  | 0.0033333 | 0.0066667
2/22/2014 | 4.8 | 576 | 115.2 | 2419.2 |  | 0.02 | 0.04
2/23/2014 | 14.6 | 1752 | 350.4 | 2769.6 |  | 0.060833 | 0.12167
2/24/2014 | 6.8 | 816 | 163.2 | 2932.8 |  | 0.028333 | 0.056667
2/25/2014 | 0 | 0 | 0 | 2932.8 |  | 0 | 0
2/26/2014 | 0.8 | 96 | 19.2 | 2952 |  | 0.0033333 | 0.0066667
2/27/2014 | 0 | 0 | 0 | 2952 |  | 0 | 0
2/28/2014 | 0.4 | 48 | 9.6 | 2961.6 |  | 0.0016667 | 0.0033333
3/1/2014 | 2 | 240 | 48 | 48 | 1 | 0.0083333 | 0.016667
3/2/2014 | 19 | 2280 | 456 | 504 |  | 0.079167 | 0.15833
3/3/2014 | 1 | 120 | 24 | 528 |  | 0.0041667 | 0.0083333
3/4/2014 | 2.4 | 288 | 57.6 | 585.6 |  | 0.01 | 0.02
3/5/2014 | 23.8 | 2856 | 571.2 | 1156.8 |  | 0.099167 | 0.19833
3/6/2014 | 8.6 | 1032 | 206.4 | 1363.2 |  | 0.035833 | 0.071667
3/7/2014 | 34 | 4080 | 816 | 2179.2 |  | 0.14167 | 0.28333
3/8/2014 | 52.4 | 6288 | 1257.6 | 1257.6 | 1 | 0.21833 | 0.43667
3/9/2014 | 10.6 | 1272 | 254.4 | 1512 |  | 0.044167 | 0.088333
3/10/2014 | 2.4 | 288 | 57.6 | 1569.6 |  | 0.01 | 0.02
3/11/2014 | 0 | 0 | 0 | 1569.6 |  | 0 | 0
3/12/2014 | 2.8 | 336 | 67.2 | 1636.8 |  | 0.011667 | 0.023333
3/13/2014 | 20.2 | 2424 | 484.8 | 2121.6 |  | 0.084167 | 0.16833
3/14/2014 | 13.8 | 1656 | 331.2 | 2452.8 |  | 0.0575 | 0.115
3/15/2014 | 22.8 | 2736 | 547.2 | 547.2 | 1 | 0.095 | 0.19
3/16/2014 | 5.4 | 648 | 129.6 | 676.8 |  | 0.0225 | 0.045
3/17/2014 | 0.4 | 48 | 9.6 | 686.4 |  | 0.0016667 | 0.0033333
3/18/2014 | 31 | 3720 | 744 | 1430.4 |  | 0.12917 | 0.25833
3/19/2014 | 1.6 | 192 | 38.4 | 1468.8 |  | 0.0066667 | 0.013333
3/20/2014 | 1.6 | 192 | 38.4 | 1507.2 |  | 0.0066667 | 0.013333
3/21/2014 | 7.6 | 912 | 182.4 | 1689.6 |  | 0.031667 | 0.063333
3/22/2014 | 2.6 | 312 | 62.4 | 1752 |  | 0.010833 | 0.021667
3/23/2014 | 0 | 0 | 0 | 1752 |  | 0 | 0
3/24/2014 | 4 | 480 | 96 | 1848 |  | 0.016667 | 0.033333
3/25/2014 | 31 | 3720 | 744 | 2592 |  | 0.12917 | 0.25833
3/26/2014 | 0.2 | 24 | 4.8 | 2596.8 |  | 0.00083333 | 0.0016667
3/27/2014 | 4.4 | 528 | 105.6 | 2702.4 |  | 0.018333 | 0.036667
3/28/2014 | 23.6 | 2832 | 566.4 | 566.4 | 1 | 0.098333 | 0.19667
3/29/2014 | 41.6 | 4992 | 998.4 | 1564.8 |  | 0.17333 | 0.34667
3/30/2014 | 3 | 360 | 72 | 1636.8 |  | 0.0125 | 0.025
3/31/2014 | 0 | 0 | 0 | 1636.8 |  | 0 | 0
4/1/2014 | 0 | 0 | 0 | 1636.8 |  | 0 | 0
4/2/2014 | 5.6 | 672 | 134.4 | 1771.2 |  | 0.023333 | 0.046667
4/3/2014 | 20.4 | 2448 | 489.6 | 2260.8 |  | 0.085 | 0.17
4/4/2014 | 2.6 | 312 | 62.4 | 2323.2 |  | 0.010833 | 0.021667
4/5/2014 | 15.9 | 1908 | 381.6 | 2704.8 |  | 0.06625 | 0.1325
4/6/2014 | 9.4 | 1128 | 225.6 | 2930.4 |  | 0.039167 | 0.078333
4/7/2014 | 13.6 | 1632 | 326.4 | 326.4 | 1 | 0.056667 | 0.11333
4/8/2014 | 5.6 | 672 | 134.4 | 460.8 |  | 0.023333 | 0.046667
4/9/2014 | 0 | 0 | 0 | 460.8 |  | 0 | 0
4/10/2014 | 16.6 | 1992 | 398.4 | 859.2 |  | 0.069167 | 0.13833
4/11/2014 | 0 | 0 | 0 | 859.2 |  | 0 | 0
4/12/2014 | 0 | 0 | 0 | 859.2 |  | 0 | 0
4/13/2014 | 0 | 0 | 0 | 859.2 |  | 0 | 0
4/14/2014 | 14.8 | 1776 | 355.2 | 1214.4 |  | 0.061667 | 0.12333
4/15/2014 | 20.8 | 2496 | 499.2 | 1713.6 |  | 0.086667 | 0.17333
4/16/2014 | 37.4 | 4488 | 897.6 | 2611.2 |  | 0.15583 | 0.31167
4/17/2014 | 9.8 | 1176 | 235.2 | 2846.4 |  | 0.040833 | 0.081667
4/18/2014 | 1.9 | 228 | 45.6 | 2892 |  | 0.0079167 | 0.015833
4/19/2014 | 21 | 2520 | 504 | 504 | 1 | 0.0875 | 0.175
4/20/2014 | 30 | 3600 | 720 | 1224 |  | 0.125 | 0.25
4/21/2014 | 0 | 0 | 0 | 1224 |  | 0 | 0
4/22/2014 | 4.4 | 528 | 105.6 | 1329.6 |  | 0.018333 | 0.036667
4/23/2014 | 12.8 | 1536 | 307.2 | 1636.8 |  | 0.053333 | 0.10667
4/24/2014 | 26 | 3120 | 624 | 2260.8 |  | 0.10833 | 0.21667
4/25/2014 | 1.8 | 216 | 43.2 | 2304 |  | 0.0075 | 0.015
4/26/2014 | 35 | 4200 | 840 | 840 | 1 | 0.14583 | 0.29167
4/27/2014 | 7.2 | 864 | 172.8 | 1012.8 |  | 0.03 | 0.06
4/28/2014 | 0.8 | 96 | 19.2 | 1032 |  | 0.0033333 | 0.0066667
4/29/2014 | 0.1 | 12 | 2.4 | 1034.4 |  | 0.00041667 | 0.00083333
4/30/2014 | 0 | 0 | 0 | 1034.4 |  | 0 | 0
5/1/2014 | 0 | 0 | 0 | 1034.4 |  | 0 | 0
5/2/2014 | 2 | 240 | 48 | 1082.4 |  | 0.0083333 | 0.016667
5/3/2014 | 4.6 | 552 | 110.4 | 1192.8 |  | 0.019167 | 0.038333
5/4/2014 | 3.8 | 456 | 91.2 | 1284 |  | 0.015833 | 0.031667
5/5/2014 | 0 | 0 | 0 | 1284 |  | 0 | 0
5/6/2014 | 0 | 0 | 0 | 1284 |  | 0 | 0
5/7/2014 | 0 | 0 | 0 | 1284 |  | 0 | 0
5/8/2014 | 0 | 0 | 0 | 1284 |  | 0 | 0
5/9/2014 | 0 | 0 | 0 | 1284 |  | 0 | 0
5/10/2014 | 0.2 | 24 | 4.8 | 1288.8 |  | 0.00083333 | 0.0016667
5/11/2014 | 0 | 0 | 0 | 1288.8 |  | 0 | 0
5/12/2014 | 0.2 | 24 | 4.8 | 1293.6 |  | 0.00083333 | 0.0016667
5/13/2014 | 0 | 0 | 0 | 1293.6 |  | 0 | 0
5/14/2014 | 0 | 0 | 0 | 1293.6 |  | 0 | 0
5/15/2014 | 0 | 0 | 0 | 1293.6 |  | 0 | 0
5/16/2014 | 2.8 | 336 | 67.2 | 1360.8 |  | 0.011667 | 0.023333
5/17/2014 | 0 | 0 | 0 | 1360.8 |  | 0 | 0
5/18/2014 | 0 | 0 | 0 | 1360.8 |  | 0 | 0
5/19/2014 | 0 | 0 | 0 | 1360.8 |  | 0 | 0
5/20/2014 | 0 | 0 | 0 | 1360.8 |  | 0 | 0
5/21/2014 | 8.2 | 984 | 196.8 | 1557.6 |  | 0.034167 | 0.068333
5/22/2014 | 29.6 | 3552 | 710.4 | 2268 |  | 0.12333 | 0.24667
5/23/2014 | 0.8 | 96 | 19.2 | 2287.2 |  | 0.0033333 | 0.0066667
5/24/2014 | 5.2 | 624 | 124.8 | 2412 |  | 0.021667 | 0.043333
5/25/2014 | 23.4 | 2808 | 561.6 | 2973.6 |  | 0.0975 | 0.195
5/26/2014 | 0 | 0 | 0 | 2973.6 |  | 0 | 0
5/27/2014 | 4.4 | 528 | 105.6 | 105.6 | 1 | 0.018333 | 0.036667
5/28/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
5/29/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
5/30/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
5/31/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/1/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/2/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/3/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/4/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/5/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/6/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/7/2014 | 0 | 0 | 0 | 105.6 |  | 0 | 0
6/8/2014 | 0.2 | 24 | 4.8 | 110.4 |  | 0.00083333 | 0.0016667
6/9/2014 | 0 | 0 | 0 | 110.4 |  | 0 | 0
6/10/2014 | 0 | 0 | 0 | 110.4 |  | 0 | 0
6/11/2014 | 0 | 0 | 0 | 110.4 |  | 0 | 0
6/12/2014 | 0 | 0 | 0 | 110.4 |  | 0 | 0
6/13/2014 | 0 | 0 | 0 | 110.4 |  | 0 | 0
6/14/2014 | 3.6 | 432 | 86.4 | 196.8 |  | 0.015 | 0.03
6/15/2014 | 0 | 0 | 0 | 196.8 |  | 0 | 0
6/16/2014 | 0 | 0 | 0 | 196.8 |  | 0 | 0
6/17/2014 | 0 | 0 | 0 | 196.8 |  | 0 | 0
6/18/2014 | 1.6 | 192 | 38.4 | 235.2 |  | 0.0066667 | 0.013333
6/19/2014 | 20.8 | 2496 | 499.2 | 734.4 |  | 0.086667 | 0.17333
6/20/2014 | 3.2 | 384 | 76.8 | 811.2 |  | 0.013333 | 0.026667
6/21/2014 | 1.2 | 144 | 28.8 | 840 |  | 0.005 | 0.01
6/22/2014 | 0 | 0 | 0 | 840 |  | 0 | 0
6/23/2014 | 15.4 | 1848 | 369.6 | 1209.6 |  | 0.064167 | 0.12833
6/24/2014 | 1.2 | 144 | 28.8 | 1238.4 |  | 0.005 | 0.01
6/25/2014 | 0 | 0 | 0 | 1238.4 |  | 0 | 0
6/26/2014 | 5.8 | 696 | 139.2 | 1377.6 |  | 0.024167 | 0.048333
6/27/2014 | 20.4 | 2448 | 489.6 | 1867.2 |  | 0.085 | 0.17
6/28/2014 | 20.4 | 2448 | 489.6 | 2356.8 |  | 0.085 | 0.17
6/29/2014 | 0.6 | 72 | 14.4 | 2371.2 |  | 0.0025 | 0.005
6/30/2014 | 0 | 0 | 0 | 2371.2 |  | 0 | 0
7/1/2014 | 0 | 0 | 0 | 2371.2 |  | 0 | 0
7/2/2014 | 1.8 | 216 | 43.2 | 2414.4 |  | 0.0075 | 0.015
7/3/2014 | 6.2 | 744 | 148.8 | 2563.2 |  | 0.025833 | 0.051667
7/4/2014 | 9.4 | 1128 | 225.6 | 2788.8 |  | 0.039167 | 0.078333
7/5/2014 | 26.6 | 3192 | 638.4 | 638.4 | 1 | 0.11083 | 0.22167
7/6/2014 | 13.6 | 1632 | 326.4 | 964.8 |  | 0.056667 | 0.11333
7/7/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/8/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/9/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/10/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/11/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/12/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/13/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/14/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/15/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/16/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/17/2014 | 0 | 0 | 0 | 964.8 |  | 0 | 0
7/18/2014 | 37 | 4440 | 888 | 1852.8 |  | 0.15417 | 0.30833
7/19/2014 | 1.8 | 216 | 43.2 | 1896 |  | 0.0075 | 0.015
7/20/2014 | 0 | 0 | 0 | 1896 |  | 0 | 0
7/21/2014 | 0 | 0 | 0 | 1896 |  | 0 | 0
7/22/2014 | 8 | 960 | 192 | 2088 |  | 0.033333 | 0.066667
7/23/2014 | 18.2 | 2184 | 436.8 | 2524.8 |  | 0.075833 | 0.15167
7/24/2014 | 0.6 | 72 | 14.4 | 2539.2 |  | 0.0025 | 0.005
7/25/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/26/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/27/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/28/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/29/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/30/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
7/31/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/1/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/2/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/3/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/4/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/5/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/6/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/7/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/8/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/9/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/10/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/11/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/12/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/13/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/14/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/15/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/16/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/17/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/18/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/19/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/20/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/21/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/22/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/23/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/24/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/25/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/26/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/27/2014 | 0 | 0 | 0 | 2539.2 |  | 0 | 0
8/28/2014 | 0.4 | 48 | 9.6 | 2548.8 |  | 0.0016667 | 0.0033333
8/29/2014 | 7.8 | 936 | 187.2 | 2736 |  | 0.0325 | 0.065
8/30/2014 | 3.6 | 432 | 86.4 | 2822.4 |  | 0.015 | 0.03
8/31/2014 | 10.6 | 1272 | 254.4 | 254.4 | 1 | 0.044167 | 0.088333
9/1/2014 | 3.2 | 384 | 76.8 | 331.2 |  | 0.013333 | 0.026667
9/2/2014 | 6.2 | 744 | 148.8 | 480 |  | 0.025833 | 0.051667
9/3/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/4/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/5/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/6/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/7/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/8/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/9/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/10/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/11/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/12/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/13/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/14/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/15/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/16/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/17/2014 | 0 | 0 | 0 | 480 |  | 0 | 0
9/18/2014 | 26.4 | 3168 | 633.6 | 1113.6 |  | 0.11 | 0.22
9/19/2014 | 0.4 | 48 | 9.6 | 1123.2 |  | 0.0016667 | 0.0033333
9/20/2014 | 0 | 0 | 0 | 1123.2 |  | 0 | 0
9/21/2014 | 2 | 240 | 48 | 1171.2 |  | 0.0083333 | 0.016667
9/22/2014 | 12.4 | 1488 | 297.6 | 1468.8 |  | 0.051667 | 0.10333
9/23/2014 | 29.4 | 3528 | 705.6 | 2174.4 |  | 0.1225 | 0.245
9/24/2014 | 1.6 | 192 | 38.4 | 2212.8 |  | 0.0066667 | 0.013333
9/25/2014 | 0.6 | 72 | 14.4 | 2227.2 |  | 0.0025 | 0.005
9/26/2014 | 8.2 | 984 | 196.8 | 2424 |  | 0.034167 | 0.068333
9/27/2014 | 0 | 0 | 0 | 2424 |  | 0 | 0
9/28/2014 | 12.4 | 1488 | 297.6 | 2721.6 |  | 0.051667 | 0.10333
9/29/2014 | 5.6 | 672 | 134.4 | 2856 |  | 0.023333 | 0.046667
9/30/2014 | 0 | 0 | 0 | 2856 |  | 0 | 0
10/1/2014 | 0 | 0 | 0 | 2856 |  | 0 | 0
10/2/2014 | 0 | 0 | 0 | 2856 |  | 0 | 0
10/3/2014 | 57.8 | 6936 | 1387.2 | 1387.2 | 1 | 0.24083 | 0.48167
10/4/2014 | 6 | 720 | 144 | 1531.2 |  | 0.025 | 0.05
10/5/2014 | 9.2 | 1104 | 220.8 | 1752 |  | 0.038333 | 0.076667
10/6/2014 | 0.4 | 48 | 9.6 | 1761.6 |  | 0.0016667 | 0.0033333
10/7/2014 | 0 | 0 | 0 | 1761.6 |  | 0 | 0
10/8/2014 | 1.4 | 168 | 33.6 | 1795.2 |  | 0.0058333 | 0.011667
10/9/2014 | 1.8 | 216 | 43.2 | 1838.4 |  | 0.0075 | 0.015
10/10/2014 | 17.8 | 2136 | 427.2 | 2265.6 |  | 0.074167 | 0.14833
10/11/2014 | 15.4 | 1848 | 369.6 | 2635.2 |  | 0.064167 | 0.12833
10/12/2014 | 33 | 3960 | 792 | 792 | 1 | 0.1375 | 0.275
10/13/2014 | 31.4 | 3768 | 753.6 | 1545.6 |  | 0.13083 | 0.26167
10/14/2014 | 28.4 | 3408 | 681.6 | 2227.2 |  | 0.11833 | 0.23667
10/15/2014 | 6.4 | 768 | 153.6 | 2380.8 |  | 0.026667 | 0.053333
10/16/2014 | 17.2 | 2064 | 412.8 | 2793.6 |  | 0.071667 | 0.14333
10/17/2014 | 27 | 3240 | 648 | 648 | 1 | 0.1125 | 0.225
10/18/2014 | 16.8 | 2016 | 403.2 | 1051.2 |  | 0.07 | 0.14
10/19/2014 | 46.2 | 5544 | 1108.8 | 2160 |  | 0.1925 | 0.385
10/20/2014 | 10.8 | 1296 | 259.2 | 2419.2 |  | 0.045 | 0.09
10/21/2014 | 40.2 | 4824 | 964.8 | 964.8 | 1 | 0.1675 | 0.335
10/22/2014 | 21.4 | 2568 | 513.6 | 1478.4 |  | 0.089167 | 0.17833
10/23/2014 | 9.4 | 1128 | 225.6 | 1704 |  | 0.039167 | 0.078333
10/24/2014 | 1.6 | 192 | 38.4 | 1742.4 |  | 0.0066667 | 0.013333
10/25/2014 | 21.8 | 2616 | 523.2 | 2265.6 |  | 0.090833 | 0.18167
10/26/2014 | 2.4 | 288 | 57.6 | 2323.2 |  | 0.01 | 0.02
10/27/2014 | 33.6 | 4032 | 806.4 | 806.4 | 1 | 0.14 | 0.28
10/28/2014 | 24.4 | 2928 | 585.6 | 1392 |  | 0.10167 | 0.20333
10/29/2014 | 7 | 840 | 168 | 1560 |  | 0.029167 | 0.058333
10/30/2014 | 9 | 1080 | 216 | 1776 |  | 0.0375 | 0.075
10/31/2014 | 15 | 1800 | 360 | 2136 |  | 0.0625 | 0.125
11/1/2014 | 6.4 | 768 | 153.6 | 2289.6 |  | 0.026667 | 0.053333
11/2/2014 | 37.6 | 4512 | 902.4 | 902.4 | 1 | 0.15667 | 0.31333
11/3/2014 | 35.2 | 4224 | 844.8 | 1747.2 |  | 0.14667 | 0.29333
11/4/2014 | 9 | 1080 | 216 | 1963.2 |  | 0.0375 | 0.075
11/5/2014 | 4.4 | 528 | 105.6 | 2068.8 |  | 0.018333 | 0.036667
11/6/2014 | 20.2 | 2424 | 484.8 | 2553.6 |  | 0.084167 | 0.16833
11/7/2014 | 1.4 | 168 | 33.6 | 2587.2 |  | 0.0058333 | 0.011667
11/8/2014 | 34 | 4080 | 816 | 816 | 1 | 0.14167 | 0.28333
11/9/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/10/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/11/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/12/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/13/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/14/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/15/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/16/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/17/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/18/2014 | 0 | 0 | 0 | 816 |  | 0 | 0
11/19/2014 | 3.4 | 408 | 81.6 | 897.6 |  | 0.014167 | 0.028333
11/20/2014 | 29.4 | 3528 | 705.6 | 1603.2 |  | 0.1225 | 0.245
11/21/2014 | 32.8 | 3936 | 787.2 | 2390.4 |  | 0.13667 | 0.27333
11/22/2014 | 25.6 | 3072 | 614.4 | 614.4 | 1 | 0.10667 | 0.21333
11/23/2014 | 15.2 | 1824 | 364.8 | 979.2 |  | 0.063333 | 0.12667
11/24/2014 | 60.6 | 7272 | 1454.4 | 2433.6 |  | 0.2525 | 0.505
11/25/2014 | 15 | 1800 | 360 | 2793.6 |  | 0.0625 | 0.125
11/26/2014 | 43 | 5160 | 1032 | 1032 | 1 | 0.17917 | 0.35833
11/27/2014 | 15 | 1800 | 360 | 1392 |  | 0.0625 | 0.125
11/28/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
11/29/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
11/30/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
12/1/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
12/2/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
12/3/2014 | 0 | 0 | 0 | 1392 |  | 0 | 0
12/4/2014 | 1.2 | 144 | 28.8 | 1420.8 |  | 0.005 | 0.01
12/5/2014 | 45.4 | 5448 | 1089.6 | 2510.4 |  | 0.18917 | 0.37833
12/6/2014 | 0.8 | 96 | 19.2 | 2529.6 |  | 0.0033333 | 0.0066667
12/7/2014 | 15.2 | 1824 | 364.8 | 2894.4 |  | 0.063333 | 0.12667
12/8/2014 | 48.6 | 5832 | 1166.4 | 1166.4 | 1 | 0.2025 | 0.405
12/9/2014 | 34.2 | 4104 | 820.8 | 1987.2 |  | 0.1425 | 0.285
12/10/2014 | 4.4 | 528 | 105.6 | 2092.8 |  | 0.018333 | 0.036667
12/11/2014 | 17.8 | 2136 | 427.2 | 2520 |  | 0.074167 | 0.14833
12/12/2014 | 1.4 | 168 | 33.6 | 2553.6 |  | 0.0058333 | 0.011667
12/13/2014 | 1 | 120 | 24 | 2577.6 |  | 0.0041667 | 0.0083333
12/14/2014 | 0 | 0 | 0 | 2577.6 |  | 0 | 0
12/15/2014 | 9 | 1080 | 216 | 2793.6 |  | 0.0375 | 0.075
12/16/2014 | 20.2 | 2424 | 484.8 | 484.8 | 1 | 0.084167 | 0.16833
12/17/2014 | 0.8 | 96 | 19.2 | 504 |  | 0.0033333 | 0.0066667
12/18/2014 | 24.6 | 2952 | 590.4 | 1094.4 |  | 0.1025 | 0.205
12/19/2014 | 0 | 0 | 0 | 1094.4 |  | 0 | 0
12/20/2014 | 0 | 0 | 0 | 1094.4 |  | 0 | 0
12/21/2014 | 8.8 | 1056 | 211.2 | 1305.6 |  | 0.036667 | 0.073333
12/22/2014 | 11.6 | 1392 | 278.4 | 1584 |  | 0.048333 | 0.096667
12/23/2014 | 10 | 1200 | 240 | 1824 |  | 0.041667 | 0.083333
12/24/2014 | 2.2 | 264 | 52.8 | 1876.8 |  | 0.0091667 | 0.018333
12/25/2014 | 0.6 | 72 | 14.4 | 1891.2 |  | 0.0025 | 0.005
12/26/2014 | 10.2 | 1224 | 244.8 | 2136 |  | 0.0425 | 0.085
12/27/2014 | 5.4 | 648 | 129.6 | 2265.6 |  | 0.0225 | 0.045
12/28/2014 | 0 | 0 | 0 | 2265.6 |  | 0 | 0
12/29/2014 | 0 | 0 | 0 | 2265.6 |  | 0 | 0
12/30/2014 | 0 | 0 | 0 | 2265.6 |  | 0 | 0
12/31/2014 | 0 | 0 | 0 | 2265.6 |  | 0 | 0

## Power
Parameters | Value | Units |  |  | Solar Panel Specs |  |  |  | Battery Specs |  |  |  | DC-AC Inverter Specs |  |  |  | Diesel Generator Specs |  |  |  | Usage over 5 years |  |  | Diesel Option Costs (5 years) |  |  | Power costs
Power Strategy | Diesel |  |  |  | Model | N/A |  |  | Energy Storage | 7200000 | J/Battery |  | Efficiency | 92% |  |  | Efficiency | 35% |  |  | Number of oil changes | 3.4115 |  | Generator | 3250 |  | Diesel | 6192.4198
Power Required | 120 | V |  |  | Area | 2 | m^2 |  | Efficiency | 96% |  |  | Cost | 2369 | $ |  | Diesel Energy | 40 | MJ/L |  | Number of times of refuelling | 8.5288 |  | Cost of changing oil | 170.5751 |  | Solar | 0
| 12 | V |  |  | Efficiency | 13% |  |  | GHG emissions | 240 | kgCO2e |  | GHG Emissions | 100 | kgCO2e |  | Oil Change Frequency | 250 | [per 250L comsumed] |  |  |  |  | Diesel costs ($) | 2771.8447 |  | Battery | 780
| 120 | V |  |  | GHG emissions | 620 | kgCO2e |  | Cost | 390 | $ | [5 empty] | Oil Change Cost | 50 | $ |  |  |  |  | Total Cost of running generator (stated duration) | 6192.4198 |  | Total | 6972.4198
Catchment Area | 120 |  |  |  | Cost of 1 panel | 450 | $ |  | Number of Batteries | 2 | [6 empty] | Refuelling | 100 | L
Volume Catchment | 10000 | L |  |  | Cost of all panels | 0 | $ |  | Total Storage | 14400000 | J | [5 empty] | GHG Emissions | 1250 | kgCO2e |  |  |  |  | Solar option costs (5 years) | 0
Pump efficiency | 70% |  |  |  | Number of Panels |  |  |  | Total Storage (MJ) | 14.4 | MJ | [5 empty] | Upfront Cost | 3250 | $
UV Lamp Load | 36 | W |  |  | Maintenance | 4 | Operations/Year |  | Total Storage (Whr) | 4000 | Whr | [5 empty] | Diesel Cost | 3.25 | $/L |  |  |  | Whr to MJ Conversion
EUV | 864 | Whr |  |  | Average Solar Intensity | 350 | W/m^2 | [9 empty] | Diesel Reliability | 365 | days/year (always 100%) |  |  |  | Whr | MJ
[5 empty] | Reliablity | 0 | days/year | [15 empty] | 1 | 0.0036
Station 1 - 2014 |  |  |  | Solar Power | [7 empty] | Solar Power in MJ | [6 empty] | Diesel Power | [5 empty] | Amount of Diesel for 1 yr (L) | 170.5751
Date | Daily Rainfall (mm) | Qin(L/day) | Qin(m^3/day) | Hours of daylight | Solar Energy (Whr) | Esolar | Ewater | Eelec | Eout | Estored |  | Solar Energy (MJ) | Esolar | Ewater | Eelec | Eout | Estored |  | pump energy (Whr) | ozone energy (Whr) | uv energy (Whr) | Daily Energy for Pump (MJ) | E consumed from battery (ozone and UV) (MJ) | Amount of Diesel Required (L) | Amount of Diesel for 5 yrs (L) | 852.8753
1/1/2014 | 18.8 | 2256 | 2.256 | 8 | 0 | 0 | 96135.9552 | 137337.0789 | 155155.567 | 0 |  | 0 | 0 | 346.0894 | 494.4135 | 558.56 | 0 |  | 137.3371 | 0 | 864 | 0.49441 | 3.1104 | 0.26674
1/2/2014 | 19.8 | 2376 | 2.376 | 8 | 0 | 0 | 101249.5699 | 144642.2427 | 163360.727 | 0 |  | 0 | 0 | 364.4985 | 520.7121 | 588.0986 | 0 |  | 144.6422 | 0 | 864 | 3.6311 | 3.1104 | 0.49079
1/3/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/4/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/5/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/6/2014 | 5 | 600 | 0.6 | 8 | 0 | 0 | 25568.0732 | 36525.8189 | 41924.3598 | 0 |  | 0 | 0 | 92.0451 | 131.4929 | 150.9277 | 0 |  | 36.5258 | 0 | 864 | 3.2419 | 3.1104 | 0.46299
1/7/2014 | 20.4 | 2448 | 2.448 | 8 | 0 | 0 | 104317.7387 | 149025.341 | 168283.823 | 0 |  | 0 | 0 | 375.5439 | 536.4912 | 605.8218 | 0 |  | 149.0253 | 0 | 864 | 3.6469 | 3.1104 | 0.49192
1/8/2014 | 24.8 | 2976 | 2.976 | 8 | 0 | 0 | 126817.6431 | 181168.0616 | 204386.5267 | 0 |  | 0 | 0 | 456.5435 | 652.205 | 735.7915 | 0 |  | 181.1681 | 0 | 864 | 3.7626 | 3.1104 | 0.50019
1/9/2014 | 34 | 4080 | 4.08 | 8 | 0 | 0 | 173862.8978 | 248375.5683 | 279873.9983 | 0 |  | 0 | 0 | 625.9064 | 894.152 | 1007.5464 | 0 |  | 248.3756 | 0 | 864 | 4.0046 | 3.1104 | 0.51747
1/10/2014 | 44.6 | 5352 | 5.352 | 8 | 0 | 0 | 228067.213 | 325810.3042 | 366848.6937 | 0 |  | 0 | 0 | 821.042 | 1172.9171 | 1320.6553 | 0 |  | 325.8103 | 0 | 864 | 4.2833 | 3.1104 | 0.53738
1/11/2014 | 14.4 | 1728 | 1.728 | 8 | 0 | 0 | 73636.0508 | 105194.3583 | 119052.8633 | 0 |  | 0 | 0 | 265.0898 | 378.6997 | 428.5903 | 0 |  | 105.1944 | 0 | 864 | 3.4891 | 3.1104 | 0.48065
1/12/2014 | 50.2 | 6024 | 6.024 | 8 | 0 | 0 | 256703.455 | 366719.2214 | 412797.5894 | 0 |  | 0 | 0 | 924.1324 | 1320.1892 | 1486.0713 | 0 |  | 366.7192 | 0 | 864 | 4.4306 | 3.1104 | 0.5479
1/13/2014 | 9.6 | 1152 | 1.152 | 8 | 0 | 0 | 49090.7006 | 70129.5722 | 79668.0955 | 0 |  | 0 | 0 | 176.7265 | 252.4665 | 286.8051 | 0 |  | 70.1296 | 0 | 864 | 3.3629 | 3.1104 | 0.47163
1/14/2014 | 5.8 | 696 | 0.696 | 8 | 0 | 0 | 29658.9649 | 42369.9499 | 48488.4877 | 0 |  | 0 | 0 | 106.7723 | 152.5318 | 174.5586 | 0 |  | 42.3699 | 0 | 864 | 3.2629 | 3.1104 | 0.4645
1/15/2014 | 1.6 | 192 | 0.192 | 8 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
1/16/2014 | 0.8 | 96 | 0.096 | 8 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
1/17/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/18/2014 | 2.6 | 312 | 0.312 | 8 | 0 | 0 | 13295.3981 | 18993.4258 | 22231.9759 | 0 |  | 0 | 0 | 47.8634 | 68.3763 | 80.0351 | 0 |  | 18.9934 | 0 | 864 | 3.1788 | 3.1104 | 0.45848
1/19/2014 | 1 | 120 | 0.12 | 8 | 0 | 0 | 5113.6146 | 7305.1638 | 9103.7199 | 0 |  | 0 | 0 | 18.409 | 26.2986 | 32.7734 | 0 |  | 7.3052 | 0 | 864 | 3.1367 | 3.1104 | 0.45548
1/20/2014 | 0.6 | 72 | 0.072 | 8 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
1/21/2014 | 0.8 | 96 | 0.096 | 8 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
1/22/2014 | 0.6 | 72 | 0.072 | 8 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
1/23/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/24/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/25/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/26/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/27/2014 | 17.6 | 2112 | 2.112 | 8 | 0 | 0 | 89999.6177 | 128570.8824 | 145309.3751 | 0 |  | 0 | 0 | 323.9986 | 462.8552 | 523.1138 | 0 |  | 128.5709 | 0 | 864 | 3.5733 | 3.1104 | 0.48666
1/28/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/29/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/30/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
1/31/2014 | 2.6 | 312 | 0.312 | 8 | 0 | 0 | 13295.3981 | 18993.4258 | 22231.9759 | 0 |  | 0 | 0 | 47.8634 | 68.3763 | 80.0351 | 0 |  | 18.9934 | 0 | 864 | 3.1788 | 3.1104 | 0.45848
2/1/2014 | 2.6 | 312 | 0.312 | 10 | 0 | 0 | 13295.3981 | 18993.4258 | 22231.9759 | 0 |  | 0 | 0 | 47.8634 | 68.3763 | 80.0351 | 0 |  | 18.9934 | 0 | 864 | 3.1788 | 3.1104 | 0.45848
2/2/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/3/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/4/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/5/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/6/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/7/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/8/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/9/2014 | 12.2 | 1464 | 1.464 | 10 | 0 | 0 | 62386.0986 | 89122.998 | 101001.5114 | 0 |  | 0 | 0 | 224.59 | 320.8428 | 363.6054 | 0 |  | 89.123 | 0 | 864 | 3.4312 | 3.1104 | 0.47652
2/10/2014 | 13.4 | 1608 | 1.608 | 10 | 0 | 0 | 68522.4362 | 97889.1946 | 110847.7033 | 0 |  | 0 | 0 | 246.6808 | 352.4011 | 399.0517 | 0 |  | 97.8892 | 0 | 864 | 3.4628 | 3.1104 | 0.47877
2/11/2014 | 46.6 | 5592 | 5.592 | 10 | 0 | 0 | 238294.4423 | 340420.6318 | 383259.0136 | 0 |  | 0 | 0 | 857.86 | 1225.5143 | 1379.7324 | 0 |  | 340.4206 | 0 | 864 | 4.3359 | 3.1104 | 0.54114
2/12/2014 | 16.8 | 2016 | 2.016 | 10 | 0 | 0 | 85908.726 | 122726.7514 | 138745.2471 | 0 |  | 0 | 0 | 309.2714 | 441.8163 | 499.4829 | 0 |  | 122.7268 | 0 | 864 | 3.5522 | 3.1104 | 0.48516
2/13/2014 | 15.6 | 1872 | 1.872 | 10 | 0 | 0 | 79772.3884 | 113960.5548 | 128899.0552 | 0 |  | 0 | 0 | 287.1806 | 410.258 | 464.0366 | 0 |  | 113.9606 | 0 | 864 | 3.5207 | 3.1104 | 0.4829
2/14/2014 | 3 | 360 | 0.36 | 10 | 0 | 0 | 15340.8439 | 21915.4913 | 25514.0399 | 0 |  | 0 | 0 | 55.227 | 78.8958 | 91.8505 | 0 |  | 21.9155 | 0 | 864 | 3.1893 | 3.1104 | 0.45924
2/15/2014 | 11.6 | 1392 | 1.392 | 10 | 0 | 0 | 59317.9298 | 84739.8998 | 96078.4154 | 0 |  | 0 | 0 | 213.5445 | 305.0636 | 345.8823 | 0 |  | 84.7399 | 0 | 864 | 3.4155 | 3.1104 | 0.47539
2/16/2014 | 19 | 2280 | 2.28 | 10 | 0 | 0 | 97158.6782 | 138798.1117 | 156796.599 | 0 |  | 0 | 0 | 349.7712 | 499.6732 | 564.4678 | 0 |  | 138.7981 | 0 | 864 | 3.6101 | 3.1104 | 0.48929
2/17/2014 | 9.2 | 1104 | 1.104 | 10 | 0 | 0 | 47045.2547 | 67207.5067 | 76386.0315 | 0 |  | 0 | 0 | 169.3629 | 241.947 | 274.9897 | 0 |  | 67.2075 | 0 | 864 | 3.3523 | 3.1104 | 0.47088
2/18/2014 | 12.6 | 1512 | 1.512 | 10 | 0 | 0 | 64431.5445 | 92045.0635 | 104283.5754 | 0 |  | 0 | 0 | 231.9536 | 331.3622 | 375.4209 | 0 |  | 92.0451 | 0 | 864 | 3.4418 | 3.1104 | 0.47727
2/19/2014 | 21.8 | 2616 | 2.616 | 10 | 0 | 0 | 111476.7992 | 159252.5702 | 179771.0469 | 0 |  | 0 | 0 | 401.3165 | 573.3093 | 647.1758 | 0 |  | 159.2526 | 0 | 864 | 3.6837 | 3.1104 | 0.49455
2/20/2014 | 2.4 | 288 | 0.288 | 10 | 0 | 0 | 12272.6751 | 17532.393 | 20590.9439 | 0 |  | 0 | 0 | 44.1816 | 63.1166 | 74.1274 | 0 |  | 17.5324 | 0 | 864 | 3.1735 | 3.1104 | 0.45811
2/21/2014 | 0.8 | 96 | 0.096 | 10 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
2/22/2014 | 4.8 | 576 | 0.576 | 10 | 0 | 0 | 24545.3503 | 35064.7861 | 40283.3278 | 0 |  | 0 | 0 | 88.3633 | 126.2332 | 145.02 | 0 |  | 35.0648 | 0 | 864 | 3.2366 | 3.1104 | 0.46262
2/23/2014 | 14.6 | 1752 | 1.752 | 10 | 0 | 0 | 74658.7737 | 106655.3911 | 120693.8953 | 0 |  | 0 | 0 | 268.7716 | 383.9594 | 434.498 | 0 |  | 106.6554 | 0 | 864 | 3.4944 | 3.1104 | 0.48103
2/24/2014 | 6.8 | 816 | 0.816 | 10 | 0 | 0 | 34772.5796 | 49675.1136 | 56693.6476 | 0 |  | 0 | 0 | 125.1813 | 178.8304 | 204.0971 | 0 |  | 49.6751 | 0 | 864 | 3.2892 | 3.1104 | 0.46637
2/25/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/26/2014 | 0.8 | 96 | 0.096 | 10 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
2/27/2014 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
2/28/2014 | 0.4 | 48 | 0.048 | 10 | 0 | 0 | 2045.4459 | 2922.0655 | 4180.624 | 0 |  | 0 | 0 | 7.3636 | 10.5194 | 15.0502 | 0 |  | 2.9221 | 0 | 864 | 3.1209 | 3.1104 | 0.45435
3/1/2014 | 2 | 240 | 0.24 | 12 | 0 | 0 | 10227.2293 | 14610.3275 | 17308.8799 | 0 |  | 0 | 0 | 36.818 | 52.5972 | 62.312 | 0 |  | 14.6103 | 0 | 864 | 3.163 | 3.1104 | 0.45736
3/2/2014 | 19 | 2280 | 2.28 | 12 | 0 | 0 | 97158.6782 | 138798.1117 | 156796.599 | 0 |  | 0 | 0 | 349.7712 | 499.6732 | 564.4678 | 0 |  | 138.7981 | 0 | 864 | 3.6101 | 3.1104 | 0.48929
3/3/2014 | 1 | 120 | 0.12 | 12 | 0 | 0 | 5113.6146 | 7305.1638 | 9103.7199 | 0 |  | 0 | 0 | 18.409 | 26.2986 | 32.7734 | 0 |  | 7.3052 | 0 | 864 | 3.1367 | 3.1104 | 0.45548
3/4/2014 | 2.4 | 288 | 0.288 | 12 | 0 | 0 | 12272.6751 | 17532.393 | 20590.9439 | 0 |  | 0 | 0 | 44.1816 | 63.1166 | 74.1274 | 0 |  | 17.5324 | 0 | 864 | 3.1735 | 3.1104 | 0.45811
3/5/2014 | 23.8 | 2856 | 2.856 | 12 | 0 | 0 | 121704.0284 | 173862.8978 | 196181.3668 | 0 |  | 0 | 0 | 438.1345 | 625.9064 | 706.2529 | 0 |  | 173.8629 | 0 | 864 | 3.7363 | 3.1104 | 0.49831
3/6/2014 | 8.6 | 1032 | 1.032 | 12 | 0 | 0 | 43977.0859 | 62824.4084 | 71462.9356 | 0 |  | 0 | 0 | 158.3175 | 226.1679 | 257.2666 | 0 |  | 62.8244 | 0 | 864 | 3.3366 | 3.1104 | 0.46975
3/7/2014 | 34 | 4080 | 4.08 | 12 | 0 | 0 | 173862.8978 | 248375.5683 | 279873.9983 | 0 |  | 0 | 0 | 625.9064 | 894.152 | 1007.5464 | 0 |  | 248.3756 | 0 | 864 | 4.0046 | 3.1104 | 0.51747
3/8/2014 | 52.4 | 6288 | 6.288 | 12 | 0 | 0 | 267953.4072 | 382790.5817 | 430848.9413 | 0 |  | 0 | 0 | 964.6323 | 1378.0461 | 1551.0562 | 0 |  | 382.7906 | 0 | 864 | 4.4884 | 3.1104 | 0.55203
3/9/2014 | 10.6 | 1272 | 1.272 | 12 | 0 | 0 | 54204.3152 | 77434.736 | 87873.2555 | 0 |  | 0 | 0 | 195.1355 | 278.765 | 316.3437 | 0 |  | 77.4347 | 0 | 864 | 3.3892 | 3.1104 | 0.47351
3/10/2014 | 2.4 | 288 | 0.288 | 12 | 0 | 0 | 12272.6751 | 17532.393 | 20590.9439 | 0 |  | 0 | 0 | 44.1816 | 63.1166 | 74.1274 | 0 |  | 17.5324 | 0 | 864 | 3.1735 | 3.1104 | 0.45811
3/11/2014 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
3/12/2014 | 2.8 | 336 | 0.336 | 12 | 0 | 0 | 14318.121 | 20454.4586 | 23873.0079 | 0 |  | 0 | 0 | 51.5452 | 73.6361 | 85.9428 | 0 |  | 20.4545 | 0 | 864 | 3.184 | 3.1104 | 0.45886
3/13/2014 | 20.2 | 2424 | 2.424 | 12 | 0 | 0 | 103295.0157 | 147564.3082 | 166642.791 | 0 |  | 0 | 0 | 371.8621 | 531.2315 | 599.914 | 0 |  | 147.5643 | 0 | 864 | 3.6416 | 3.1104 | 0.49155
3/14/2014 | 13.8 | 1656 | 1.656 | 12 | 0 | 0 | 70567.882 | 100811.2601 | 114129.7673 | 0 |  | 0 | 0 | 254.0444 | 362.9205 | 410.8672 | 0 |  | 100.8113 | 0 | 864 | 3.4733 | 3.1104 | 0.47952
3/15/2014 | 22.8 | 2736 | 2.736 | 12 | 0 | 0 | 116590.4138 | 166557.734 | 187976.2068 | 0 |  | 0 | 0 | 419.7255 | 599.6078 | 676.7143 | 0 |  | 166.5577 | 0 | 864 | 3.71 | 3.1104 | 0.49643
3/16/2014 | 5.4 | 648 | 0.648 | 12 | 0 | 0 | 27613.5191 | 39447.8844 | 45206.4237 | 0 |  | 0 | 0 | 99.4087 | 142.0124 | 162.7431 | 0 |  | 39.4479 | 0 | 864 | 3.2524 | 3.1104 | 0.46374
3/17/2014 | 0.4 | 48 | 0.048 | 12 | 0 | 0 | 2045.4459 | 2922.0655 | 4180.624 | 0 |  | 0 | 0 | 7.3636 | 10.5194 | 15.0502 | 0 |  | 2.9221 | 0 | 864 | 3.1209 | 3.1104 | 0.45435
3/18/2014 | 31 | 3720 | 3.72 | 12 | 0 | 0 | 158522.0539 | 226460.0769 | 255258.5184 | 0 |  | 0 | 0 | 570.6794 | 815.2563 | 918.9307 | 0 |  | 226.4601 | 0 | 864 | 3.9257 | 3.1104 | 0.51183
3/19/2014 | 1.6 | 192 | 0.192 | 12 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
3/20/2014 | 1.6 | 192 | 0.192 | 12 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
3/21/2014 | 7.6 | 912 | 0.912 | 12 | 0 | 0 | 38863.4713 | 55519.2447 | 63257.7756 | 0 |  | 0 | 0 | 139.9085 | 199.8693 | 227.728 | 0 |  | 55.5192 | 0 | 864 | 3.3103 | 3.1104 | 0.46788
3/22/2014 | 2.6 | 312 | 0.312 | 12 | 0 | 0 | 13295.3981 | 18993.4258 | 22231.9759 | 0 |  | 0 | 0 | 47.8634 | 68.3763 | 80.0351 | 0 |  | 18.9934 | 0 | 864 | 3.1788 | 3.1104 | 0.45848
3/23/2014 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
3/24/2014 | 4 | 480 | 0.48 | 12 | 0 | 0 | 20454.4586 | 29220.6551 | 33719.1998 | 0 |  | 0 | 0 | 73.6361 | 105.1944 | 121.3891 | 0 |  | 29.2207 | 0 | 864 | 3.2156 | 3.1104 | 0.46111
3/25/2014 | 31 | 3720 | 3.72 | 12 | 0 | 0 | 158522.0539 | 226460.0769 | 255258.5184 | 0 |  | 0 | 0 | 570.6794 | 815.2563 | 918.9307 | 0 |  | 226.4601 | 0 | 864 | 3.9257 | 3.1104 | 0.51183
3/26/2014 | 0.2 | 24 | 0.024 | 12 | 0 | 0 | 1022.7229 | 1461.0328 | 2539.592 | 0 |  | 0 | 0 | 3.6818 | 5.2597 | 9.1425 | 0 |  | 1.461 | 0 | 864 | 3.1157 | 3.1104 | 0.45398
3/27/2014 | 4.4 | 528 | 0.528 | 12 | 0 | 0 | 22499.9044 | 32142.7206 | 37001.2638 | 0 |  | 0 | 0 | 80.9997 | 115.7138 | 133.2045 | 0 |  | 32.1427 | 0 | 864 | 3.2261 | 3.1104 | 0.46187
3/28/2014 | 23.6 | 2832 | 2.832 | 12 | 0 | 0 | 120681.3055 | 172401.865 | 194540.3348 | 0 |  | 0 | 0 | 434.4527 | 620.6467 | 700.3452 | 0 |  | 172.4019 | 0 | 864 | 3.731 | 3.1104 | 0.49793
3/29/2014 | 41.6 | 4992 | 4.992 | 12 | 0 | 0 | 212726.369 | 303894.8129 | 342233.2139 | 0 |  | 0 | 0 | 765.8149 | 1094.0213 | 1232.0396 | 0 |  | 303.8948 | 0 | 864 | 4.2044 | 3.1104 | 0.53174
3/30/2014 | 3 | 360 | 0.36 | 12 | 0 | 0 | 15340.8439 | 21915.4913 | 25514.0399 | 0 |  | 0 | 0 | 55.227 | 78.8958 | 91.8505 | 0 |  | 21.9155 | 0 | 864 | 3.1893 | 3.1104 | 0.45924
3/31/2014 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/1/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/2/2014 | 5.6 | 672 | 0.672 | 14 | 0 | 0 | 28636.242 | 40908.9171 | 46847.4557 | 0 |  | 0 | 0 | 103.0905 | 147.2721 | 168.6508 | 0 |  | 40.9089 | 0 | 864 | 3.2577 | 3.1104 | 0.46412
4/3/2014 | 20.4 | 2448 | 2.448 | 14 | 0 | 0 | 104317.7387 | 149025.341 | 168283.823 | 0 |  | 0 | 0 | 375.5439 | 536.4912 | 605.8218 | 0 |  | 149.0253 | 0 | 864 | 3.6469 | 3.1104 | 0.49192
4/4/2014 | 2.6 | 312 | 0.312 | 14 | 0 | 0 | 13295.3981 | 18993.4258 | 22231.9759 | 0 |  | 0 | 0 | 47.8634 | 68.3763 | 80.0351 | 0 |  | 18.9934 | 0 | 864 | 3.1788 | 3.1104 | 0.45848
4/5/2014 | 15.9 | 1908 | 1.908 | 14 | 0 | 0 | 81306.4728 | 116152.104 | 131360.6032 | 0 |  | 0 | 0 | 292.7033 | 418.1476 | 472.8982 | 0 |  | 116.1521 | 0 | 864 | 3.5285 | 3.1104 | 0.48347
4/6/2014 | 9.4 | 1128 | 1.128 | 14 | 0 | 0 | 48067.9776 | 68668.5395 | 78027.0635 | 0 |  | 0 | 0 | 173.0447 | 247.2067 | 280.8974 | 0 |  | 68.6685 | 0 | 864 | 3.3576 | 3.1104 | 0.47126
4/7/2014 | 13.6 | 1632 | 1.632 | 14 | 0 | 0 | 69545.1591 | 99350.2273 | 112488.7353 | 0 |  | 0 | 0 | 250.3626 | 357.6608 | 404.9594 | 0 |  | 99.3502 | 0 | 864 | 3.4681 | 3.1104 | 0.47915
4/8/2014 | 5.6 | 672 | 0.672 | 14 | 0 | 0 | 28636.242 | 40908.9171 | 46847.4557 | 0 |  | 0 | 0 | 103.0905 | 147.2721 | 168.6508 | 0 |  | 40.9089 | 0 | 864 | 3.2577 | 3.1104 | 0.46412
4/9/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/10/2014 | 16.6 | 1992 | 1.992 | 14 | 0 | 0 | 84886.003 | 121265.7186 | 137104.2152 | 0 |  | 0 | 0 | 305.5896 | 436.5566 | 493.5752 | 0 |  | 121.2657 | 0 | 864 | 3.547 | 3.1104 | 0.48478
4/11/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/12/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/13/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/14/2014 | 14.8 | 1776 | 1.776 | 14 | 0 | 0 | 75681.4967 | 108116.4238 | 122334.9272 | 0 |  | 0 | 0 | 272.4534 | 389.2191 | 440.4057 | 0 |  | 108.1164 | 0 | 864 | 3.4996 | 3.1104 | 0.4814
4/15/2014 | 20.8 | 2496 | 2.496 | 14 | 0 | 0 | 106363.1845 | 151947.4065 | 171565.8869 | 0 |  | 0 | 0 | 382.9075 | 547.0107 | 617.6372 | 0 |  | 151.9474 | 0 | 864 | 3.6574 | 3.1104 | 0.49267
4/16/2014 | 37.4 | 4488 | 4.488 | 14 | 0 | 0 | 191249.1876 | 273213.1251 | 307771.5421 | 0 |  | 0 | 0 | 688.4971 | 983.5673 | 1107.9776 | 0 |  | 273.2131 | 0 | 864 | 4.094 | 3.1104 | 0.52385
4/17/2014 | 9.8 | 1176 | 1.176 | 14 | 0 | 0 | 50113.4235 | 71590.605 | 81309.1275 | 0 |  | 0 | 0 | 180.4083 | 257.7262 | 292.7129 | 0 |  | 71.5906 | 0 | 864 | 3.3681 | 3.1104 | 0.47201
4/18/2014 | 1.9 | 228 | 0.228 | 14 | 0 | 0 | 9715.8678 | 13879.8112 | 16488.3639 | 0 |  | 0 | 0 | 34.9771 | 49.9673 | 59.3581 | 0 |  | 13.8798 | 0 | 864 | 3.1604 | 3.1104 | 0.45717
4/19/2014 | 21 | 2520 | 2.52 | 14 | 0 | 0 | 107385.9075 | 153408.4392 | 173206.9189 | 0 |  | 0 | 0 | 386.5893 | 552.2704 | 623.5449 | 0 |  | 153.4084 | 0 | 864 | 3.6627 | 3.1104 | 0.49305
4/20/2014 | 30 | 3600 | 3.6 | 14 | 0 | 0 | 153408.4392 | 219154.9132 | 247053.3585 | 0 |  | 0 | 0 | 552.2704 | 788.9577 | 889.3921 | 0 |  | 219.1549 | 0 | 864 | 3.8994 | 3.1104 | 0.50995
4/21/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
4/22/2014 | 4.4 | 528 | 0.528 | 14 | 0 | 0 | 22499.9044 | 32142.7206 | 37001.2638 | 0 |  | 0 | 0 | 80.9997 | 115.7138 | 133.2045 | 0 |  | 32.1427 | 0 | 864 | 3.2261 | 3.1104 | 0.46187
4/23/2014 | 12.8 | 1536 | 1.536 | 14 | 0 | 0 | 65454.2674 | 93506.0963 | 105924.6073 | 0 |  | 0 | 0 | 235.6354 | 336.6219 | 381.3286 | 0 |  | 93.5061 | 0 | 864 | 3.447 | 3.1104 | 0.47764
4/24/2014 | 26 | 3120 | 3.12 | 14 | 0 | 0 | 132953.9807 | 189934.2581 | 214232.7187 | 0 |  | 0 | 0 | 478.6343 | 683.7633 | 771.2378 | 0 |  | 189.9343 | 0 | 864 | 3.7942 | 3.1104 | 0.50244
4/25/2014 | 1.8 | 216 | 0.216 | 14 | 0 | 0 | 9204.5064 | 13149.2948 | 15667.8479 | 0 |  | 0 | 0 | 33.1362 | 47.3375 | 56.4043 | 0 |  | 13.1493 | 0 | 864 | 3.1577 | 3.1104 | 0.45698
4/26/2014 | 35 | 4200 | 4.2 | 14 | 0 | 0 | 178976.5124 | 255680.732 | 288079.1582 | 0 |  | 0 | 0 | 644.3154 | 920.4506 | 1037.085 | 0 |  | 255.6807 | 0 | 864 | 4.0309 | 3.1104 | 0.51935
4/27/2014 | 7.2 | 864 | 0.864 | 14 | 0 | 0 | 36818.0254 | 52597.1792 | 59975.7116 | 0 |  | 0 | 0 | 132.5449 | 189.3498 | 215.9126 | 0 |  | 52.5972 | 0 | 864 | 3.2997 | 3.1104 | 0.46712
4/28/2014 | 0.8 | 96 | 0.096 | 14 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
4/29/2014 | 0.1 | 12 | 0.012 | 14 | 0 | 0 | 511.3615 | 730.5164 | 1719.076 | 0 |  | 0 | 0 | 1.8409 | 2.6299 | 6.1887 | 0 |  | 0.73052 | 0 | 864 | 3.113 | 3.1104 | 0.45379
4/30/2014 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/1/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/2/2014 | 2 | 240 | 0.24 | 15 | 0 | 0 | 10227.2293 | 14610.3275 | 17308.8799 | 0 |  | 0 | 0 | 36.818 | 52.5972 | 62.312 | 0 |  | 14.6103 | 0 | 864 | 3.163 | 3.1104 | 0.45736
5/3/2014 | 4.6 | 552 | 0.552 | 15 | 0 | 0 | 23522.6273 | 33603.7533 | 38642.2958 | 0 |  | 0 | 0 | 84.6815 | 120.9735 | 139.1123 | 0 |  | 33.6038 | 0 | 864 | 3.2314 | 3.1104 | 0.46224
5/4/2014 | 3.8 | 456 | 0.456 | 15 | 0 | 0 | 19431.7356 | 27759.6223 | 32078.1678 | 0 |  | 0 | 0 | 69.9542 | 99.9346 | 115.4814 | 0 |  | 27.7596 | 0 | 864 | 3.2103 | 3.1104 | 0.46074
5/5/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/6/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/7/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/8/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/9/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/10/2014 | 0.2 | 24 | 0.024 | 15 | 0 | 0 | 1022.7229 | 1461.0328 | 2539.592 | 0 |  | 0 | 0 | 3.6818 | 5.2597 | 9.1425 | 0 |  | 1.461 | 0 | 864 | 3.1157 | 3.1104 | 0.45398
5/11/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/12/2014 | 0.2 | 24 | 0.024 | 15 | 0 | 0 | 1022.7229 | 1461.0328 | 2539.592 | 0 |  | 0 | 0 | 3.6818 | 5.2597 | 9.1425 | 0 |  | 1.461 | 0 | 864 | 3.1157 | 3.1104 | 0.45398
5/13/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/14/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/15/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/16/2014 | 2.8 | 336 | 0.336 | 15 | 0 | 0 | 14318.121 | 20454.4586 | 23873.0079 | 0 |  | 0 | 0 | 51.5452 | 73.6361 | 85.9428 | 0 |  | 20.4545 | 0 | 864 | 3.184 | 3.1104 | 0.45886
5/17/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/18/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/19/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/20/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/21/2014 | 8.2 | 984 | 0.984 | 15 | 0 | 0 | 41931.6401 | 59902.3429 | 68180.8716 | 0 |  | 0 | 0 | 150.9539 | 215.6484 | 245.4511 | 0 |  | 59.9023 | 0 | 864 | 3.326 | 3.1104 | 0.469
5/22/2014 | 29.6 | 3552 | 3.552 | 15 | 0 | 0 | 151362.9934 | 216232.8477 | 243771.2945 | 0 |  | 0 | 0 | 544.9068 | 778.4383 | 877.5767 | 0 |  | 216.2328 | 0 | 864 | 3.8888 | 3.1104 | 0.5092
5/23/2014 | 0.8 | 96 | 0.096 | 15 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
5/24/2014 | 5.2 | 624 | 0.624 | 15 | 0 | 0 | 26590.7961 | 37986.8516 | 43565.3917 | 0 |  | 0 | 0 | 95.7269 | 136.7527 | 156.8354 | 0 |  | 37.9869 | 0 | 864 | 3.2472 | 3.1104 | 0.46337
5/25/2014 | 23.4 | 2808 | 2.808 | 15 | 0 | 0 | 119658.5826 | 170940.8323 | 192899.3028 | 0 |  | 0 | 0 | 430.7709 | 615.387 | 694.4375 | 0 |  | 170.9408 | 0 | 864 | 3.7258 | 3.1104 | 0.49756
5/26/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/27/2014 | 4.4 | 528 | 0.528 | 15 | 0 | 0 | 22499.9044 | 32142.7206 | 37001.2638 | 0 |  | 0 | 0 | 80.9997 | 115.7138 | 133.2045 | 0 |  | 32.1427 | 0 | 864 | 3.2261 | 3.1104 | 0.46187
5/28/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/29/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/30/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
5/31/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/1/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/2/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/3/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/4/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/5/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/6/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/7/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/8/2014 | 0.2 | 24 | 0.024 | 15 | 0 | 0 | 1022.7229 | 1461.0328 | 2539.592 | 0 |  | 0 | 0 | 3.6818 | 5.2597 | 9.1425 | 0 |  | 1.461 | 0 | 864 | 3.1157 | 3.1104 | 0.45398
6/9/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/10/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/11/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/12/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/13/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/14/2014 | 3.6 | 432 | 0.432 | 15 | 0 | 0 | 18409.0127 | 26298.5896 | 30437.1358 | 0 |  | 0 | 0 | 66.2724 | 94.6749 | 109.5737 | 0 |  | 26.2986 | 0 | 864 | 3.2051 | 3.1104 | 0.46036
6/15/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/16/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/17/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/18/2014 | 1.6 | 192 | 0.192 | 15 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
6/19/2014 | 20.8 | 2496 | 2.496 | 15 | 0 | 0 | 106363.1845 | 151947.4065 | 171565.8869 | 0 |  | 0 | 0 | 382.9075 | 547.0107 | 617.6372 | 0 |  | 151.9474 | 0 | 864 | 3.6574 | 3.1104 | 0.49267
6/20/2014 | 3.2 | 384 | 0.384 | 15 | 0 | 0 | 16363.5668 | 23376.5241 | 27155.0718 | 0 |  | 0 | 0 | 58.9088 | 84.1555 | 97.7583 | 0 |  | 23.3765 | 0 | 864 | 3.1946 | 3.1104 | 0.45961
6/21/2014 | 1.2 | 144 | 0.144 | 15 | 0 | 0 | 6136.3376 | 8766.1965 | 10744.7519 | 0 |  | 0 | 0 | 22.0908 | 31.5583 | 38.6811 | 0 |  | 8.7662 | 0 | 864 | 3.142 | 3.1104 | 0.45585
6/22/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/23/2014 | 15.4 | 1848 | 1.848 | 15 | 0 | 0 | 78749.6655 | 112499.5221 | 127258.0232 | 0 |  | 0 | 0 | 283.4988 | 404.9983 | 458.1289 | 0 |  | 112.4995 | 0 | 864 | 3.5154 | 3.1104 | 0.48253
6/24/2014 | 1.2 | 144 | 0.144 | 15 | 0 | 0 | 6136.3376 | 8766.1965 | 10744.7519 | 0 |  | 0 | 0 | 22.0908 | 31.5583 | 38.6811 | 0 |  | 8.7662 | 0 | 864 | 3.142 | 3.1104 | 0.45585
6/25/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
6/26/2014 | 5.8 | 696 | 0.696 | 15 | 0 | 0 | 29658.9649 | 42369.9499 | 48488.4877 | 0 |  | 0 | 0 | 106.7723 | 152.5318 | 174.5586 | 0 |  | 42.3699 | 0 | 864 | 3.2629 | 3.1104 | 0.4645
6/27/2014 | 20.4 | 2448 | 2.448 | 15 | 0 | 0 | 104317.7387 | 149025.341 | 168283.823 | 0 |  | 0 | 0 | 375.5439 | 536.4912 | 605.8218 | 0 |  | 149.0253 | 0 | 864 | 3.6469 | 3.1104 | 0.49192
6/28/2014 | 20.4 | 2448 | 2.448 | 15 | 0 | 0 | 104317.7387 | 149025.341 | 168283.823 | 0 |  | 0 | 0 | 375.5439 | 536.4912 | 605.8218 | 0 |  | 149.0253 | 0 | 864 | 3.6469 | 3.1104 | 0.49192
6/29/2014 | 0.6 | 72 | 0.072 | 15 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
6/30/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/1/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/2/2014 | 1.8 | 216 | 0.216 | 15 | 0 | 0 | 9204.5064 | 13149.2948 | 15667.8479 | 0 |  | 0 | 0 | 33.1362 | 47.3375 | 56.4043 | 0 |  | 13.1493 | 0 | 864 | 3.1577 | 3.1104 | 0.45698
7/3/2014 | 6.2 | 744 | 0.744 | 15 | 0 | 0 | 31704.4108 | 45292.0154 | 51770.5517 | 0 |  | 0 | 0 | 114.1359 | 163.0513 | 186.374 | 0 |  | 45.292 | 0 | 864 | 3.2735 | 3.1104 | 0.46525
7/4/2014 | 9.4 | 1128 | 1.128 | 15 | 0 | 0 | 48067.9776 | 68668.5395 | 78027.0635 | 0 |  | 0 | 0 | 173.0447 | 247.2067 | 280.8974 | 0 |  | 68.6685 | 0 | 864 | 3.3576 | 3.1104 | 0.47126
7/5/2014 | 26.6 | 3192 | 3.192 | 15 | 0 | 0 | 136022.1494 | 194317.3563 | 219155.8146 | 0 |  | 0 | 0 | 489.6797 | 699.5425 | 788.9609 | 0 |  | 194.3174 | 0 | 864 | 3.8099 | 3.1104 | 0.50357
7/6/2014 | 13.6 | 1632 | 1.632 | 15 | 0 | 0 | 69545.1591 | 99350.2273 | 112488.7353 | 0 |  | 0 | 0 | 250.3626 | 357.6608 | 404.9594 | 0 |  | 99.3502 | 0 | 864 | 3.4681 | 3.1104 | 0.47915
7/7/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/8/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/9/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/10/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/11/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/12/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/13/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/14/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/15/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/16/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/17/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/18/2014 | 37 | 4440 | 4.44 | 15 | 0 | 0 | 189203.7417 | 270291.0596 | 304489.4781 | 0 |  | 0 | 0 | 681.1335 | 973.0478 | 1096.1621 | 0 |  | 270.2911 | 0 | 864 | 4.0834 | 3.1104 | 0.5231
7/19/2014 | 1.8 | 216 | 0.216 | 15 | 0 | 0 | 9204.5064 | 13149.2948 | 15667.8479 | 0 |  | 0 | 0 | 33.1362 | 47.3375 | 56.4043 | 0 |  | 13.1493 | 0 | 864 | 3.1577 | 3.1104 | 0.45698
7/20/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/21/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/22/2014 | 8 | 960 | 0.96 | 15 | 0 | 0 | 40908.9171 | 58441.3102 | 66539.8396 | 0 |  | 0 | 0 | 147.2721 | 210.3887 | 239.5434 | 0 |  | 58.4413 | 0 | 864 | 3.3208 | 3.1104 | 0.46863
7/23/2014 | 18.2 | 2184 | 2.184 | 15 | 0 | 0 | 93067.7865 | 132953.9807 | 150232.4711 | 0 |  | 0 | 0 | 335.044 | 478.6343 | 540.8369 | 0 |  | 132.954 | 0 | 864 | 3.589 | 3.1104 | 0.48779
7/24/2014 | 0.6 | 72 | 0.072 | 15 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
7/25/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/26/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/27/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/28/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/29/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/30/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
7/31/2014 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/1/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/2/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/3/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/4/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/5/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/6/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/7/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/8/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/9/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/10/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/11/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/12/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/13/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/14/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/15/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/16/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/17/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/18/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/19/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/20/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/21/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/22/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/23/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/24/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/25/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/26/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/27/2014 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
8/28/2014 | 0.4 | 48 | 0.048 | 14.5 | 0 | 0 | 2045.4459 | 2922.0655 | 4180.624 | 0 |  | 0 | 0 | 7.3636 | 10.5194 | 15.0502 | 0 |  | 2.9221 | 0 | 864 | 3.1209 | 3.1104 | 0.45435
8/29/2014 | 7.8 | 936 | 0.936 | 14.5 | 0 | 0 | 39886.1942 | 56980.2774 | 64898.8076 | 0 |  | 0 | 0 | 143.5903 | 205.129 | 233.6357 | 0 |  | 56.9803 | 0 | 864 | 3.3155 | 3.1104 | 0.46825
8/30/2014 | 3.6 | 432 | 0.432 | 14.5 | 0 | 0 | 18409.0127 | 26298.5896 | 30437.1358 | 0 |  | 0 | 0 | 66.2724 | 94.6749 | 109.5737 | 0 |  | 26.2986 | 0 | 864 | 3.2051 | 3.1104 | 0.46036
8/31/2014 | 10.6 | 1272 | 1.272 | 14.5 | 0 | 0 | 54204.3152 | 77434.736 | 87873.2555 | 0 |  | 0 | 0 | 195.1355 | 278.765 | 316.3437 | 0 |  | 77.4347 | 0 | 864 | 3.3892 | 3.1104 | 0.47351
9/1/2014 | 3.2 | 384 | 0.384 | 13 | 0 | 0 | 16363.5668 | 23376.5241 | 27155.0718 | 0 |  | 0 | 0 | 58.9088 | 84.1555 | 97.7583 | 0 |  | 23.3765 | 0 | 864 | 3.1946 | 3.1104 | 0.45961
9/2/2014 | 6.2 | 744 | 0.744 | 13 | 0 | 0 | 31704.4108 | 45292.0154 | 51770.5517 | 0 |  | 0 | 0 | 114.1359 | 163.0513 | 186.374 | 0 |  | 45.292 | 0 | 864 | 3.2735 | 3.1104 | 0.46525
9/3/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/4/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/5/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/6/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/7/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/8/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/9/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/10/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/11/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/12/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/13/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/14/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/15/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/16/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/17/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/18/2014 | 26.4 | 3168 | 3.168 | 13 | 0 | 0 | 134999.4265 | 192856.3236 | 217514.7827 | 0 |  | 0 | 0 | 485.9979 | 694.2828 | 783.0532 | 0 |  | 192.8563 | 0 | 864 | 3.8047 | 3.1104 | 0.50319
9/19/2014 | 0.4 | 48 | 0.048 | 13 | 0 | 0 | 2045.4459 | 2922.0655 | 4180.624 | 0 |  | 0 | 0 | 7.3636 | 10.5194 | 15.0502 | 0 |  | 2.9221 | 0 | 864 | 3.1209 | 3.1104 | 0.45435
9/20/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/21/2014 | 2 | 240 | 0.24 | 13 | 0 | 0 | 10227.2293 | 14610.3275 | 17308.8799 | 0 |  | 0 | 0 | 36.818 | 52.5972 | 62.312 | 0 |  | 14.6103 | 0 | 864 | 3.163 | 3.1104 | 0.45736
9/22/2014 | 12.4 | 1488 | 1.488 | 13 | 0 | 0 | 63408.8215 | 90584.0308 | 102642.5434 | 0 |  | 0 | 0 | 228.2718 | 326.1025 | 369.5132 | 0 |  | 90.584 | 0 | 864 | 3.4365 | 3.1104 | 0.47689
9/23/2014 | 29.4 | 3528 | 3.528 | 13 | 0 | 0 | 150340.2704 | 214771.8149 | 242130.2625 | 0 |  | 0 | 0 | 541.225 | 773.1785 | 871.6689 | 0 |  | 214.7718 | 0 | 864 | 3.8836 | 3.1104 | 0.50883
9/24/2014 | 1.6 | 192 | 0.192 | 13 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
9/25/2014 | 0.6 | 72 | 0.072 | 13 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
9/26/2014 | 8.2 | 984 | 0.984 | 13 | 0 | 0 | 41931.6401 | 59902.3429 | 68180.8716 | 0 |  | 0 | 0 | 150.9539 | 215.6484 | 245.4511 | 0 |  | 59.9023 | 0 | 864 | 3.326 | 3.1104 | 0.469
9/27/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
9/28/2014 | 12.4 | 1488 | 1.488 | 13 | 0 | 0 | 63408.8215 | 90584.0308 | 102642.5434 | 0 |  | 0 | 0 | 228.2718 | 326.1025 | 369.5132 | 0 |  | 90.584 | 0 | 864 | 3.4365 | 3.1104 | 0.47689
9/29/2014 | 5.6 | 672 | 0.672 | 13 | 0 | 0 | 28636.242 | 40908.9171 | 46847.4557 | 0 |  | 0 | 0 | 103.0905 | 147.2721 | 168.6508 | 0 |  | 40.9089 | 0 | 864 | 3.2577 | 3.1104 | 0.46412
9/30/2014 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
10/1/2014 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
10/2/2014 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
10/3/2014 | 57.8 | 6936 | 6.936 | 10.5 | 0 | 0 | 295566.9262 | 422238.466 | 475156.8051 | 0 |  | 0 | 0 | 1064.0409 | 1520.0585 | 1710.5645 | 0 |  | 422.2385 | 0 | 864 | 4.6305 | 3.1104 | 0.56218
10/4/2014 | 6 | 720 | 0.72 | 10.5 | 0 | 0 | 30681.6878 | 43830.9826 | 50129.5197 | 0 |  | 0 | 0 | 110.4541 | 157.7915 | 180.4663 | 0 |  | 43.831 | 0 | 864 | 3.2682 | 3.1104 | 0.46487
10/5/2014 | 9.2 | 1104 | 1.104 | 10.5 | 0 | 0 | 47045.2547 | 67207.5067 | 76386.0315 | 0 |  | 0 | 0 | 169.3629 | 241.947 | 274.9897 | 0 |  | 67.2075 | 0 | 864 | 3.3523 | 3.1104 | 0.47088
10/6/2014 | 0.4 | 48 | 0.048 | 10.5 | 0 | 0 | 2045.4459 | 2922.0655 | 4180.624 | 0 |  | 0 | 0 | 7.3636 | 10.5194 | 15.0502 | 0 |  | 2.9221 | 0 | 864 | 3.1209 | 3.1104 | 0.45435
10/7/2014 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
10/8/2014 | 1.4 | 168 | 0.168 | 10.5 | 0 | 0 | 7159.0605 | 10227.2293 | 12385.7839 | 0 |  | 0 | 0 | 25.7726 | 36.818 | 44.5888 | 0 |  | 10.2272 | 0 | 864 | 3.1472 | 3.1104 | 0.45623
10/9/2014 | 1.8 | 216 | 0.216 | 10.5 | 0 | 0 | 9204.5064 | 13149.2948 | 15667.8479 | 0 |  | 0 | 0 | 33.1362 | 47.3375 | 56.4043 | 0 |  | 13.1493 | 0 | 864 | 3.1577 | 3.1104 | 0.45698
10/10/2014 | 17.8 | 2136 | 2.136 | 10.5 | 0 | 0 | 91022.3406 | 130031.9151 | 146950.4071 | 0 |  | 0 | 0 | 327.6804 | 468.1149 | 529.0215 | 0 |  | 130.0319 | 0 | 864 | 3.5785 | 3.1104 | 0.48704
10/11/2014 | 15.4 | 1848 | 1.848 | 10.5 | 0 | 0 | 78749.6655 | 112499.5221 | 127258.0232 | 0 |  | 0 | 0 | 283.4988 | 404.9983 | 458.1289 | 0 |  | 112.4995 | 0 | 864 | 3.5154 | 3.1104 | 0.48253
10/12/2014 | 33 | 3960 | 3.96 | 10.5 | 0 | 0 | 168749.2831 | 241070.4045 | 271668.8383 | 0 |  | 0 | 0 | 607.4974 | 867.8535 | 978.0078 | 0 |  | 241.0704 | 0 | 864 | 3.9783 | 3.1104 | 0.51559
10/13/2014 | 31.4 | 3768 | 3.768 | 10.5 | 0 | 0 | 160567.4997 | 229382.1424 | 258540.5824 | 0 |  | 0 | 0 | 578.043 | 825.7757 | 930.7461 | 0 |  | 229.3821 | 0 | 864 | 3.9362 | 3.1104 | 0.51258
10/14/2014 | 28.4 | 3408 | 3.408 | 10.5 | 0 | 0 | 145226.6558 | 207466.6511 | 233925.1026 | 0 |  | 0 | 0 | 522.816 | 746.8799 | 842.1304 | 0 |  | 207.4667 | 0 | 864 | 3.8573 | 3.1104 | 0.50695
10/15/2014 | 6.4 | 768 | 0.768 | 10.5 | 0 | 0 | 32727.1337 | 46753.0481 | 53411.5837 | 0 |  | 0 | 0 | 117.8177 | 168.311 | 192.2817 | 0 |  | 46.753 | 0 | 864 | 3.2787 | 3.1104 | 0.46562
10/16/2014 | 17.2 | 2064 | 2.064 | 10.5 | 0 | 0 | 87954.1718 | 125648.8169 | 142027.3111 | 0 |  | 0 | 0 | 316.635 | 452.3357 | 511.2983 | 0 |  | 125.6488 | 0 | 864 | 3.5627 | 3.1104 | 0.48591
10/17/2014 | 27 | 3240 | 3.24 | 10.5 | 0 | 0 | 138067.5953 | 197239.4219 | 222437.8786 | 0 |  | 0 | 0 | 497.0433 | 710.0619 | 800.7764 | 0 |  | 197.2394 | 0 | 864 | 3.8205 | 3.1104 | 0.50432
10/18/2014 | 16.8 | 2016 | 2.016 | 10.5 | 0 | 0 | 85908.726 | 122726.7514 | 138745.2471 | 0 |  | 0 | 0 | 309.2714 | 441.8163 | 499.4829 | 0 |  | 122.7268 | 0 | 864 | 3.5522 | 3.1104 | 0.48516
10/19/2014 | 46.2 | 5544 | 5.544 | 10.5 | 0 | 0 | 236248.9964 | 337498.5663 | 379976.9496 | 0 |  | 0 | 0 | 850.4964 | 1214.9948 | 1367.917 | 0 |  | 337.4986 | 0 | 864 | 4.3254 | 3.1104 | 0.54039
10/20/2014 | 10.8 | 1296 | 1.296 | 10.5 | 0 | 0 | 55227.0381 | 78895.7687 | 89514.2875 | 0 |  | 0 | 0 | 198.8173 | 284.0248 | 322.2514 | 0 |  | 78.8958 | 0 | 864 | 3.3944 | 3.1104 | 0.47389
10/21/2014 | 40.2 | 4824 | 4.824 | 10.5 | 0 | 0 | 205567.3086 | 293667.5836 | 330745.99 | 0 |  | 0 | 0 | 740.0423 | 1057.2033 | 1190.6856 | 0 |  | 293.6676 | 0 | 864 | 4.1676 | 3.1104 | 0.52911
10/22/2014 | 21.4 | 2568 | 2.568 | 10.5 | 0 | 0 | 109431.3533 | 156330.5047 | 176488.9829 | 0 |  | 0 | 0 | 393.9529 | 562.7898 | 635.3603 | 0 |  | 156.3305 | 0 | 864 | 3.6732 | 3.1104 | 0.4938
10/23/2014 | 9.4 | 1128 | 1.128 | 10.5 | 0 | 0 | 48067.9776 | 68668.5395 | 78027.0635 | 0 |  | 0 | 0 | 173.0447 | 247.2067 | 280.8974 | 0 |  | 68.6685 | 0 | 864 | 3.3576 | 3.1104 | 0.47126
10/24/2014 | 1.6 | 192 | 0.192 | 10.5 | 0 | 0 | 8181.7834 | 11688.262 | 14026.8159 | 0 |  | 0 | 0 | 29.4544 | 42.0777 | 50.4965 | 0 |  | 11.6883 | 0 | 864 | 3.1525 | 3.1104 | 0.45661
10/25/2014 | 21.8 | 2616 | 2.616 | 10.5 | 0 | 0 | 111476.7992 | 159252.5702 | 179771.0469 | 0 |  | 0 | 0 | 401.3165 | 573.3093 | 647.1758 | 0 |  | 159.2526 | 0 | 864 | 3.6837 | 3.1104 | 0.49455
10/26/2014 | 2.4 | 288 | 0.288 | 10.5 | 0 | 0 | 12272.6751 | 17532.393 | 20590.9439 | 0 |  | 0 | 0 | 44.1816 | 63.1166 | 74.1274 | 0 |  | 17.5324 | 0 | 864 | 3.1735 | 3.1104 | 0.45811
10/27/2014 | 33.6 | 4032 | 4.032 | 10.5 | 0 | 0 | 171817.4519 | 245453.5027 | 276591.9343 | 0 |  | 0 | 0 | 618.5428 | 883.6326 | 995.731 | 0 |  | 245.4535 | 0 | 864 | 3.994 | 3.1104 | 0.51672
10/28/2014 | 24.4 | 2928 | 2.928 | 10.5 | 0 | 0 | 124772.1972 | 178245.996 | 201104.4628 | 0 |  | 0 | 0 | 449.1799 | 641.6856 | 723.9761 | 0 |  | 178.246 | 0 | 864 | 3.7521 | 3.1104 | 0.49943
10/29/2014 | 7 | 840 | 0.84 | 10.5 | 0 | 0 | 35795.3025 | 51136.1464 | 58334.6796 | 0 |  | 0 | 0 | 128.8631 | 184.0901 | 210.0048 | 0 |  | 51.1361 | 0 | 864 | 3.2945 | 3.1104 | 0.46675
10/30/2014 | 9 | 1080 | 1.08 | 10.5 | 0 | 0 | 46022.5318 | 65746.4739 | 74744.9995 | 0 |  | 0 | 0 | 165.6811 | 236.6873 | 269.082 | 0 |  | 65.7465 | 0 | 864 | 3.3471 | 3.1104 | 0.47051
10/31/2014 | 15 | 1800 | 1.8 | 10.5 | 0 | 0 | 76704.2196 | 109577.4566 | 123975.9592 | 0 |  | 0 | 0 | 276.1352 | 394.4788 | 446.3135 | 0 |  | 109.5775 | 0 | 864 | 3.5049 | 3.1104 | 0.48178
11/1/2014 | 6.4 | 768 | 0.768 | 9 | 0 | 0 | 32727.1337 | 46753.0481 | 53411.5837 | 0 |  | 0 | 0 | 117.8177 | 168.311 | 192.2817 | 0 |  | 46.753 | 0 | 864 | 3.2787 | 3.1104 | 0.46562
11/2/2014 | 37.6 | 4512 | 4.512 | 9 | 0 | 0 | 192271.9105 | 274674.1578 | 309412.5741 | 0 |  | 0 | 0 | 692.1789 | 988.827 | 1113.8853 | 0 |  | 274.6742 | 0 | 864 | 4.0992 | 3.1104 | 0.52423
11/3/2014 | 35.2 | 4224 | 4.224 | 9 | 0 | 0 | 179999.2353 | 257141.7648 | 289720.1902 | 0 |  | 0 | 0 | 647.9972 | 925.7104 | 1042.9927 | 0 |  | 257.1418 | 0 | 864 | 4.0361 | 3.1104 | 0.51972
11/4/2014 | 9 | 1080 | 1.08 | 9 | 0 | 0 | 46022.5318 | 65746.4739 | 74744.9995 | 0 |  | 0 | 0 | 165.6811 | 236.6873 | 269.082 | 0 |  | 65.7465 | 0 | 864 | 3.3471 | 3.1104 | 0.47051
11/5/2014 | 4.4 | 528 | 0.528 | 9 | 0 | 0 | 22499.9044 | 32142.7206 | 37001.2638 | 0 |  | 0 | 0 | 80.9997 | 115.7138 | 133.2045 | 0 |  | 32.1427 | 0 | 864 | 3.2261 | 3.1104 | 0.46187
11/6/2014 | 20.2 | 2424 | 2.424 | 9 | 0 | 0 | 103295.0157 | 147564.3082 | 166642.791 | 0 |  | 0 | 0 | 371.8621 | 531.2315 | 599.914 | 0 |  | 147.5643 | 0 | 864 | 3.6416 | 3.1104 | 0.49155
11/7/2014 | 1.4 | 168 | 0.168 | 9 | 0 | 0 | 7159.0605 | 10227.2293 | 12385.7839 | 0 |  | 0 | 0 | 25.7726 | 36.818 | 44.5888 | 0 |  | 10.2272 | 0 | 864 | 3.1472 | 3.1104 | 0.45623
11/8/2014 | 34 | 4080 | 4.08 | 9 | 0 | 0 | 173862.8978 | 248375.5683 | 279873.9983 | 0 |  | 0 | 0 | 625.9064 | 894.152 | 1007.5464 | 0 |  | 248.3756 | 0 | 864 | 4.0046 | 3.1104 | 0.51747
11/9/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/10/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/11/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/12/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/13/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/14/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/15/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/16/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/17/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/18/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/19/2014 | 3.4 | 408 | 0.408 | 9 | 0 | 0 | 17386.2898 | 24837.5568 | 28796.1038 | 0 |  | 0 | 0 | 62.5906 | 89.4152 | 103.666 | 0 |  | 24.8376 | 0 | 864 | 3.1998 | 3.1104 | 0.45999
11/20/2014 | 29.4 | 3528 | 3.528 | 9 | 0 | 0 | 150340.2704 | 214771.8149 | 242130.2625 | 0 |  | 0 | 0 | 541.225 | 773.1785 | 871.6689 | 0 |  | 214.7718 | 0 | 864 | 3.8836 | 3.1104 | 0.50883
11/21/2014 | 32.8 | 3936 | 3.936 | 9 | 0 | 0 | 167726.5602 | 239609.3717 | 270027.8063 | 0 |  | 0 | 0 | 603.8156 | 862.5937 | 972.1001 | 0 |  | 239.6094 | 0 | 864 | 3.973 | 3.1104 | 0.51521
11/22/2014 | 25.6 | 3072 | 3.072 | 9 | 0 | 0 | 130908.5348 | 187012.1926 | 210950.6547 | 0 |  | 0 | 0 | 471.2707 | 673.2439 | 759.4224 | 0 |  | 187.0122 | 0 | 864 | 3.7836 | 3.1104 | 0.50169
11/23/2014 | 15.2 | 1824 | 1.824 | 9 | 0 | 0 | 77726.9425 | 111038.4893 | 125616.9912 | 0 |  | 0 | 0 | 279.817 | 399.7386 | 452.2212 | 0 |  | 111.0385 | 0 | 864 | 3.5101 | 3.1104 | 0.48215
11/24/2014 | 60.6 | 7272 | 7.272 | 9 | 0 | 0 | 309885.0472 | 442692.9246 | 498131.2529 | 0 |  | 0 | 0 | 1115.5862 | 1593.6945 | 1793.2725 | 0 |  | 442.6929 | 0 | 864 | 4.7041 | 3.1104 | 0.56744
11/25/2014 | 15 | 1800 | 1.8 | 9 | 0 | 0 | 76704.2196 | 109577.4566 | 123975.9592 | 0 |  | 0 | 0 | 276.1352 | 394.4788 | 446.3135 | 0 |  | 109.5775 | 0 | 864 | 3.5049 | 3.1104 | 0.48178
11/26/2014 | 43 | 5160 | 5.16 | 9 | 0 | 0 | 219885.4295 | 314122.0422 | 353720.4378 | 0 |  | 0 | 0 | 791.5875 | 1130.8394 | 1273.3936 | 0 |  | 314.122 | 0 | 864 | 4.2412 | 3.1104 | 0.53437
11/27/2014 | 15 | 1800 | 1.8 | 9 | 0 | 0 | 76704.2196 | 109577.4566 | 123975.9592 | 0 |  | 0 | 0 | 276.1352 | 394.4788 | 446.3135 | 0 |  | 109.5775 | 0 | 864 | 3.5049 | 3.1104 | 0.48178
11/28/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/29/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
11/30/2014 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/1/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/2/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/3/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/4/2014 | 1.2 | 144 | 0.144 | 8 | 0 | 0 | 6136.3376 | 8766.1965 | 10744.7519 | 0 |  | 0 | 0 | 22.0908 | 31.5583 | 38.6811 | 0 |  | 8.7662 | 0 | 864 | 3.142 | 3.1104 | 0.45585
12/5/2014 | 45.4 | 5448 | 5.448 | 8 | 0 | 0 | 232158.1047 | 331654.4353 | 373412.8217 | 0 |  | 0 | 0 | 835.7692 | 1193.956 | 1344.2862 | 0 |  | 331.6544 | 0 | 864 | 4.3044 | 3.1104 | 0.53888
12/6/2014 | 0.8 | 96 | 0.096 | 8 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
12/7/2014 | 15.2 | 1824 | 1.824 | 8 | 0 | 0 | 77726.9425 | 111038.4893 | 125616.9912 | 0 |  | 0 | 0 | 279.817 | 399.7386 | 452.2212 | 0 |  | 111.0385 | 0 | 864 | 3.5101 | 3.1104 | 0.48215
12/8/2014 | 48.6 | 5832 | 5.832 | 8 | 0 | 0 | 248521.6715 | 355030.9593 | 399669.3335 | 0 |  | 0 | 0 | 894.678 | 1278.1115 | 1438.8096 | 0 |  | 355.031 | 0 | 864 | 4.3885 | 3.1104 | 0.54489
12/9/2014 | 34.2 | 4104 | 4.104 | 8 | 0 | 0 | 174885.6207 | 249836.601 | 281515.0303 | 0 |  | 0 | 0 | 629.5882 | 899.4118 | 1013.4541 | 0 |  | 249.8366 | 0 | 864 | 4.0098 | 3.1104 | 0.51784
12/10/2014 | 4.4 | 528 | 0.528 | 8 | 0 | 0 | 22499.9044 | 32142.7206 | 37001.2638 | 0 |  | 0 | 0 | 80.9997 | 115.7138 | 133.2045 | 0 |  | 32.1427 | 0 | 864 | 3.2261 | 3.1104 | 0.46187
12/11/2014 | 17.8 | 2136 | 2.136 | 8 | 0 | 0 | 91022.3406 | 130031.9151 | 146950.4071 | 0 |  | 0 | 0 | 327.6804 | 468.1149 | 529.0215 | 0 |  | 130.0319 | 0 | 864 | 3.5785 | 3.1104 | 0.48704
12/12/2014 | 1.4 | 168 | 0.168 | 8 | 0 | 0 | 7159.0605 | 10227.2293 | 12385.7839 | 0 |  | 0 | 0 | 25.7726 | 36.818 | 44.5888 | 0 |  | 10.2272 | 0 | 864 | 3.1472 | 3.1104 | 0.45623
12/13/2014 | 1 | 120 | 0.12 | 8 | 0 | 0 | 5113.6146 | 7305.1638 | 9103.7199 | 0 |  | 0 | 0 | 18.409 | 26.2986 | 32.7734 | 0 |  | 7.3052 | 0 | 864 | 3.1367 | 3.1104 | 0.45548
12/14/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/15/2014 | 9 | 1080 | 1.08 | 8 | 0 | 0 | 46022.5318 | 65746.4739 | 74744.9995 | 0 |  | 0 | 0 | 165.6811 | 236.6873 | 269.082 | 0 |  | 65.7465 | 0 | 864 | 3.3471 | 3.1104 | 0.47051
12/16/2014 | 20.2 | 2424 | 2.424 | 8 | 0 | 0 | 103295.0157 | 147564.3082 | 166642.791 | 0 |  | 0 | 0 | 371.8621 | 531.2315 | 599.914 | 0 |  | 147.5643 | 0 | 864 | 3.6416 | 3.1104 | 0.49155
12/17/2014 | 0.8 | 96 | 0.096 | 8 | 0 | 0 | 4090.8917 | 5844.131 | 7462.688 | 0 |  | 0 | 0 | 14.7272 | 21.0389 | 26.8657 | 0 |  | 5.8441 | 0 | 864 | 3.1314 | 3.1104 | 0.4551
12/18/2014 | 24.6 | 2952 | 2.952 | 8 | 0 | 0 | 125794.9202 | 179707.0288 | 202745.4947 | 0 |  | 0 | 0 | 452.8617 | 646.9453 | 729.8838 | 0 |  | 179.707 | 0 | 864 | 3.7573 | 3.1104 | 0.49981
12/19/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/20/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/21/2014 | 8.8 | 1056 | 1.056 | 8 | 0 | 0 | 44999.8088 | 64285.4412 | 73103.9676 | 0 |  | 0 | 0 | 161.9993 | 231.4276 | 263.1743 | 0 |  | 64.2854 | 0 | 864 | 3.3418 | 3.1104 | 0.47013
12/22/2014 | 11.6 | 1392 | 1.392 | 8 | 0 | 0 | 59317.9298 | 84739.8998 | 96078.4154 | 0 |  | 0 | 0 | 213.5445 | 305.0636 | 345.8823 | 0 |  | 84.7399 | 0 | 864 | 3.4155 | 3.1104 | 0.47539
12/23/2014 | 10 | 1200 | 1.2 | 8 | 0 | 0 | 51136.1464 | 73051.6377 | 82950.1595 | 0 |  | 0 | 0 | 184.0901 | 262.9859 | 298.6206 | 0 |  | 73.0516 | 0 | 864 | 3.3734 | 3.1104 | 0.47238
12/24/2014 | 2.2 | 264 | 0.264 | 8 | 0 | 0 | 11249.9522 | 16071.3603 | 18949.9119 | 0 |  | 0 | 0 | 40.4998 | 57.8569 | 68.2197 | 0 |  | 16.0714 | 0 | 864 | 3.1683 | 3.1104 | 0.45773
12/25/2014 | 0.6 | 72 | 0.072 | 8 | 0 | 0 | 3068.1688 | 4383.0983 | 5821.656 | 0 |  | 0 | 0 | 11.0454 | 15.7792 | 20.958 | 0 |  | 4.3831 | 0 | 864 | 3.1262 | 3.1104 | 0.45473
12/26/2014 | 10.2 | 1224 | 1.224 | 8 | 0 | 0 | 52158.8693 | 74512.6705 | 84591.1915 | 0 |  | 0 | 0 | 187.7719 | 268.2456 | 304.5283 | 0 |  | 74.5127 | 0 | 864 | 3.3786 | 3.1104 | 0.47276
12/27/2014 | 5.4 | 648 | 0.648 | 8 | 0 | 0 | 27613.5191 | 39447.8844 | 45206.4237 | 0 |  | 0 | 0 | 99.4087 | 142.0124 | 162.7431 | 0 |  | 39.4479 | 0 | 864 | 3.2524 | 3.1104 | 0.46374
12/28/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/29/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/30/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
12/31/2014 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 898.56 | 0 |  | 0 | 0 | 0 | 0 | 3.2348 | 0 |  | 0 | 0 | 864 | 3.1104 | 3.1104 | 0.4536
[22 empty] | Total Diesel per Year: |  | 170.5751
[22 empty] | Total Diesel per 5 Years: |  | 852.8753

## GHG Emissions
Existing System
Water Treatment | 109.5 | kg | Centralized Water Treatment | 0.1 | kg/1000L
Land and Sea Transportation | 7008 | kg | Transport | 6.4 | kg/1000L
Storage and Distribution | 2408 | kg
Total Shipping Water Emissions | 9525.5 | kg
Diesel Power
Proposed System | [5 empty] | Water Consumed in 5 years | 1095000 | L
Storage and Distribution | 2408 | kg |  |  |  | GHG emission for the existing system in 5 years | 9525.5 | kg
Water Treatment | 3900.7718 | kg |  |  |  | GHG manufacturing generator | 1250 | kg
Total of System | 6308.7718 |  |  |  |  | GHG from burning diesel | 2.7718 | kg | Diesel Consumed by the generator in 5 years | 852.8753 | L
GHG from Water Treatment | [5 empty] | GHG manufacturing battery | 240 | kg
From Diesel | 3900.7718 | kg |  |  |  | CO2 emission for the RWH | 3900.7718 | kg
From Solar | 620 | kg
Solar Power
Relative GHG% | 66.23% |  |  |  |  | GHG from Production | 620 | kg

## Risk Matrices
***Column C values obtained by entering column B values into the Exposure Frequency Calculator Below
Health Risk Exposure |  |  | (Chlorine) | [5 empty] | Health Risk Exposure |  | (Chlorine)
|  |  | Irritation or Inconvenience | Minor Injury | Serious Injury | Permanent Injury or Death |  |  |  |  | Inconvenience | Minor Wounds | Serious Wounds | Permanent Wounds/Death
|  |  | 1 | 2 | 3 | 4 |  |  |  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 0.065753 | 3.9906 | 3.9906 | 7.9812 | 11.9718 | 15.9624 |  |  | Daily Risk Exposure | 0.065753 | 3.9906 | 7.9812 | 11.9718 | 15.9624
Weekly Risk Exposure | 0.46154 | 3.9341 | 3.9341 | 7.8681 | 11.8022 | 15.7363 |  |  | Weekly Risk Exposure | 0.46154 | 3.9341 | 7.8681 | 11.8022 | 15.7363
Monthly Risk Exposure | 2 | 3.7143 | 3.7143 | 7.4286 | 11.1429 | 14.8571 |  |  | Monthly Risk Exposure | 2 | 3.7143 | 7.4286 | 11.1429 | 14.8571
Annual Risk Exposure | 24 | 2.2609 | 2.2609 | 4.5217 | 6.7826 | 9.0435 | Total Health Risk Exposure |  | Annual Risk Exposure | 24 | 2.2609 | 4.5217 | 6.7826 | 9.0435
23.9598
Health Risk Exposure |  |  | (Diesel) | [5 empty] | Health Risk Exposure |  | (Diesel)
|  |  | Irritation or Inconvenience | Minor Injury | Serious Injury | Permanent Injury or Death |  |  |  |  | Inconvenience | Minor Wounds | Serious Wounds | Permanent Wounds/Death
|  |  | 1 | 2 | 3 | 4 |  |  |  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 0.0093466 | 3.9987 | 3.9987 | 7.9973 | 11.996 | 15.9947 |  |  | Daily Risk Exposure | 0.0093466 | 3.9987 | 7.9973 | 11.996 | 15.9947
Weekly Risk Exposure | 0.065606 | 3.9906 | 3.9906 | 7.9813 | 11.9719 | 15.9625 |  |  | Weekly Risk Exposure | 0.065606 | 3.9906 | 7.9813 | 11.9719 | 15.9625
Monthly Risk Exposure | 0.28429 | 3.9594 | 3.9594 | 7.9188 | 11.8782 | 15.8375 |  |  | Monthly Risk Exposure | 0.28429 | 3.9594 | 7.9188 | 11.8782 | 15.8375
Annual Risk Exposure | 3.4115 | 3.5126 | 3.5126 | 7.0253 | 10.5379 | 14.0506 |  |  | Annual Risk Exposure | 3.4115 | 3.5126 | 7.0253 | 10.5379 | 14.0506
Total Risk Exposure
47.9276
Enviro Risk Exposure |  |  | (Chlorine)
|  |  | Irritation or Inconvenience | Minor Injury | Serious Injury | Permanent Injury or Death
|  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 0.065753 | 3.9906 | 3.9906 | 7.9812 | 11.9718 | 15.9624
Weekly Risk Exposure | 0.46154 | 3.9341 | 3.9341 | 7.8681 | 11.8022 | 15.7363
Monthly Risk Exposure | 2 | 3.7143 | 3.7143 | 7.4286 | 11.1429 | 14.8571
Annual Risk Exposure | 24 | 2.2609 | 2.2609 | 4.5217 | 6.7826 | 9.0435 | Total Enviro Risk Exposure
23.9678
Enviro Risk Exposure |  |  | (Diesel)
|  |  | Irritation or Inconvenience | Minor Injury | Serious Injury | Permanent Injury or Death
|  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 0.0093466 | 3.9987 | 3.9987 | 7.9973 | 11.996 | 15.9947
Weekly Risk Exposure | 0.065606 | 3.9906 | 3.9906 | 7.9813 | 11.9719 | 15.9625
Monthly Risk Exposure | 0.28429 | 3.9594 | 3.9594 | 7.9188 | 11.8782 | 15.8375
Annual Risk Exposure | 3.4115 | 3.5126 | 3.5126 | 7.0253 | 10.5379 | 14.0506
Exposure Frequency Calculations |  | Daily Exposure Chlorine | Enter Days Here: | 0.065753 | Frequency Value: | 3.9906
Exposure Frequency Calculations |  | Weekly Exposure Chlorine | Enter Days Here: | 0.46154 | Frequency Value: | 3.9341
Exposure Frequency Calculations |  | Monthly Exposure Chlorine | Enter Days Here: | 2 | Frequency Value: | 3.7143
Exposure Frequency Calculations |  | Yearly Exposure Chlorine | Enter Days Here: | 24 | Frequency Value: | 2.2609
Exposure Frequency Calculations |  | Daily Exposure Diesel | Enter Days Here: | 0.0093466 | Frequency Value: | 3.9987
Exposure Frequency Calculations |  | Weekly Exposure Diesel | Enter Days Here: | 0.065606 | Frequency Value: | 3.9906
Exposure Frequency Calculations |  | Monthly Exposure Diesel | Enter Days Here: | 0.28429 | Frequency Value: | 3.9594
Exposure Frequency Calculations |  | Yearly Exposure Diesel | Enter Days Here: | 3.4115 | Frequency Value: | 3.5126